## directional_window_burden
sensor_id | n_windows | soft_low_window_rate | soft_high_window_rate | mean_soft_low_rate | mean_soft_high_rate | max_soft_low_exceedance | max_soft_high_exceedance | physical_low_window_rate | zero_equivalent_window_rate | zero_offset_warning_window_rate | severe_negative_window_rate | soft_low | soft_high | effective_soft_low | zero_equivalence_low | threshold_scope | soft_sensitivity_anchor | type | pool | position | process_zone
DO_1_1 | 3072 | 0.0042318 | 0.014323 | 9.1565e-05 | 0.0038158 | 0.02 | 7.3538 | 0.0042318 | 0 | 0 | 0 | 0 |  | 0 |  | temperature_conditioned_position_template | lower | DO | 1 | 1 | aerobic
DO_1_2 | 3072 | 0 | 0.019857 | 0 | 0.0044223 | 0 | 6.7639 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | temperature_conditioned_position_template | lower | DO | 1 | 2 | aerobic
DO_1_3 | 3072 | 0 | 0.00032552 | 0 | 1.0879e-05 | 0 | 2.7084 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | temperature_conditioned_position_template | lower | DO | 1 | 3 | aerobic
DO_1_4 | 3072 | 0 | 0 | 0 | 0 | 0 |  | 0.96289 | 0.96289 | 0 | 0 | 0 |  | -0.05 | -0.05 | sensor_override | none | DO | 1 | 4 | post_anoxic
DO_2_1 | 3072 | 0 | 0.026042 | 0 | 0.010733 | 0 | 7.0575 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | temperature_conditioned_position_template | lower | DO | 2 | 1 | aerobic
DO_2_2 | 3072 | 0 | 0.018229 | 0 | 0.0099168 | 0 | 2.2583 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | temperature_conditioned_position_template | lower | DO | 2 | 2 | aerobic
DO_2_3 | 3072 | 0 | 0.0068359 | 0 | 0.00094376 | 0 | 3.8864 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | temperature_conditioned_position_template | lower | DO | 2 | 3 | aerobic
DO_2_4 | 3072 | 0 | 0 | 0 | 0 | 0 |  | 0.0016276 | 0.0016276 | 0 | 0 | 0 |  | -0.05 | -0.05 | sensor_override | none | DO | 2 | 4 | post_anoxic
ORP_1_1 | 3072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -400 | 200 | -400 |  | sensor_type | center | ORP | 1 | 1 | anaerobic
ORP_1_2 | 3072 | 0.022786 | 0 | 0.010558 | 0 | 18.77 | 0 | 0.022786 | 0 | 0 | 0 | -400 | 200 | -400 |  | sensor_type | center | ORP | 1 | 2 | anoxic_mid
ORP_1_3 | 3072 | 0.1849 | 0 | 0.15305 | 0 | 100.93 | 0 | 0.1849 | 0 | 0 | 0 | -400 | 200 | -400 |  | sensor_type | center | ORP | 1 | 3 | anoxic_end
ORP_2_1 | 3072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -400 | 200 | -400 |  | sensor_type | center | ORP | 2 | 1 | anaerobic
ORP_2_2 | 3072 | 0.0026042 | 0 | 0.00068266 | 0 | 13.45 | 0 | 0.0026042 | 0 | 0 | 0 | -400 | 200 | -400 |  | sensor_type | center | ORP | 2 | 2 | anoxic_mid
ORP_2_3 | 3072 | 0.71191 | 0 | 0.61553 | 0 | 94.33 | 0 | 0.71191 | 0 | 0 | 0 | -400 | 200 | -400 |  | sensor_type | center | ORP | 2 | 3 | anoxic_end

## DO_seasonal_raw_distribution
sensor_id | process_zone | position | season | n | p95 | p99 | maximum | distribution_role
DO_1_1 | aerobic | 1 | summer | 44503 | 1.2 | 2.3298 | 9.3 | raw_context_only_temperature_envelope_audited_separately
DO_1_1 | aerobic | 1 | transition | 193609 | 1.64 | 2.78 | 10.36 | raw_context_only_temperature_envelope_audited_separately
DO_1_1 | aerobic | 1 | winter | 129022 | 1.67 | 2.07 | 10.37 | raw_context_only_temperature_envelope_audited_separately
DO_1_2 | aerobic | 2 | summer | 44504 | 1.84 | 2.42 | 3.93 | raw_context_only_temperature_envelope_audited_separately
DO_1_2 | aerobic | 2 | transition | 193610 | 2.44 | 2.95 | 9.95 | raw_context_only_temperature_envelope_audited_separately
DO_1_2 | aerobic | 2 | winter | 129022 | 2.68 | 3.52 | 10.31 | raw_context_only_temperature_envelope_audited_separately
DO_1_3 | aerobic | 3 | summer | 44501 | 1.58 | 1.89 | 2.92 | raw_context_only_temperature_envelope_audited_separately
DO_1_3 | aerobic | 3 | transition | 193610 | 3.36 | 3.83 | 8.51 | raw_context_only_temperature_envelope_audited_separately
DO_1_3 | aerobic | 3 | winter | 129022 | 3.5 | 4.1 | 5.06 | raw_context_only_temperature_envelope_audited_separately
DO_2_1 | aerobic | 1 | summer | 44510 | 1.58 | 2.57 | 4.46 | raw_context_only_temperature_envelope_audited_separately
DO_2_1 | aerobic | 1 | transition | 193600 | 2.13 | 3.48 | 10.32 | raw_context_only_temperature_envelope_audited_separately
DO_2_1 | aerobic | 1 | winter | 129022 | 1.7 | 2.2479 | 10.31 | raw_context_only_temperature_envelope_audited_separately
DO_2_2 | aerobic | 2 | summer | 44510 | 1.97 | 2.6191 | 3.85 | raw_context_only_temperature_envelope_audited_separately
DO_2_2 | aerobic | 2 | transition | 193598 | 2.22 | 3.65 | 6.05 | raw_context_only_temperature_envelope_audited_separately
DO_2_2 | aerobic | 2 | winter | 129022 | 2.2 | 2.79 | 3.62 | raw_context_only_temperature_envelope_audited_separately
DO_2_3 | aerobic | 3 | summer | 44510 | 1.64 | 2.05 | 2.85 | raw_context_only_temperature_envelope_audited_separately
DO_2_3 | aerobic | 3 | transition | 193610 | 5.08 | 5.54 | 10.31 | raw_context_only_temperature_envelope_audited_separately
DO_2_3 | aerobic | 3 | winter | 129022 | 5.01 | 5.48 | 10.31 | raw_context_only_temperature_envelope_audited_separately

## ORP_position_season_envelope
sensor_id | process_zone | position | season | n | median | mad_scale | robust_low_k3 | robust_high_k3 | p01 | p99 | below_minus_400_rate | above_200_rate | envelope_role
ORP_1_1 | anaerobic | 1 | summer | 44505 | -223.03 | 26.6275 | -302.9125 | -143.1475 | -264.2684 | -153.7316 | 0 | 0 | diagnostic_only_pending_site_review
ORP_1_1 | anaerobic | 1 | transition | 193615 | -199.93 | 66.8653 | -400.5258 | 0.66578 | -303.2172 | -61.6028 | 0 | 0 | diagnostic_only_pending_site_review
ORP_1_1 | anaerobic | 1 | winter | 129022 | -241.825 | 26.3236 | -320.7957 | -162.8543 | -288.8779 | -134.97 | 0 | 0 | diagnostic_only_pending_site_review
ORP_1_2 | anoxic_mid | 2 | summer | 44504 | -213.2 | 42.8027 | -341.608 | -84.792 | -271.2494 | -108.9015 | 0 | 0 | diagnostic_only_pending_site_review
ORP_1_2 | anoxic_mid | 2 | transition | 193611 | -147.97 | 66.8208 | -348.4323 | 52.4923 | -396.768 | -42.67 | 0.006792 | 0 | diagnostic_only_pending_site_review
ORP_1_2 | anoxic_mid | 2 | winter | 129022 | -172.23 | 67.1321 | -373.6264 | 29.1664 | -404.93 | -88.73 | 0.019896 | 0 | diagnostic_only_pending_site_review
ORP_1_3 | anoxic_end | 3 | summer | 44504 | -265.2 | 98.4446 | -560.5339 | 30.1339 | -487.1688 | -95.8 | 0.13107 | 0 | diagnostic_only_pending_site_review
ORP_1_3 | anoxic_end | 3 | transition | 193612 | -147.83 | 163.7235 | -639.0006 | 343.3406 | -499.5 | 23.95 | 0.15734 | 0 | diagnostic_only_pending_site_review
ORP_1_3 | anoxic_end | 3 | winter | 129022 | -194.07 | 66.2722 | -392.8867 | 4.7467 | -491.8779 | -19.6842 | 0.15466 | 0 | diagnostic_only_pending_site_review
ORP_2_1 | anaerobic | 1 | summer | 44509 | -247.88 | 23.8402 | -319.4006 | -176.3594 | -284.1484 | -159.808 | 0 | 0 | diagnostic_only_pending_site_review
ORP_2_1 | anaerobic | 1 | transition | 193607 | -198.4 | 53.9666 | -360.2999 | -36.5001 | -380.63 | -5.7706 | 0 | 0 | diagnostic_only_pending_site_review
ORP_2_1 | anaerobic | 1 | winter | 129022 | -214.3 | 31.9204 | -310.0611 | -118.5389 | -261.4 | -91.6542 | 0 | 0 | diagnostic_only_pending_site_review
ORP_2_2 | anoxic_mid | 2 | summer | 44508 | -336.2 | 29.059 | -423.3769 | -249.0231 | -371.1986 | -285.4207 | 0 | 0 | diagnostic_only_pending_site_review
ORP_2_2 | anoxic_mid | 2 | transition | 193607 | -280.82 | 25.8714 | -358.4341 | -203.2059 | -391.65 | -224 | 0.0012964 | 0 | diagnostic_only_pending_site_review
ORP_2_2 | anoxic_mid | 2 | winter | 129022 | -283.2 | 29.2072 | -370.8217 | -195.5783 | -385.67 | -244.58 | 0 | 0 | diagnostic_only_pending_site_review
ORP_2_3 | anoxic_end | 3 | summer | 44510 | -373.93 | 138.6528 | -789.8883 | 42.0283 | -481.55 | -3.5209 | 0.43449 | 0 | diagnostic_only_pending_site_review
ORP_2_3 | anoxic_end | 3 | transition | 193608 | -386.525 | 115.7985 | -733.9204 | -39.1296 | -478.3 | 38.5 | 0.47489 | 0 | diagnostic_only_pending_site_review
ORP_2_3 | anoxic_end | 3 | winter | 129022 | -449.6 | 6.9682 | -470.5047 | -428.6953 | -460.3958 | -218.6063 | 0.8886 | 0 | diagnostic_only_pending_site_review

## DO4_zero_eq_sensitivity
sensor_id | zero_equivalence_low_mg_L | n_observed | negative_value_rate | zero_offset_warning_rate | minimum_observed | role
DO_1_4 | 0 | 367121 | 0.25314 | 0.25314 | -0.03 | sensitivity_not_final_manufacturer_lock
DO_1_4 | -0.03 | 367121 | 0.25314 | 0 | -0.03 | sensitivity_not_final_manufacturer_lock
DO_1_4 | -0.05 | 367121 | 0.25314 | 0 | -0.03 | sensitivity_not_final_manufacturer_lock
DO_1_4 | -0.1 | 367121 | 0.25314 | 0 | -0.03 | sensitivity_not_final_manufacturer_lock
DO_2_4 | 0 | 367130 | 2.4514e-05 | 2.4514e-05 | -0.01 | sensitivity_not_final_manufacturer_lock
DO_2_4 | -0.03 | 367130 | 2.4514e-05 | 0 | -0.01 | sensitivity_not_final_manufacturer_lock
DO_2_4 | -0.05 | 367130 | 2.4514e-05 | 0 | -0.01 | sensitivity_not_final_manufacturer_lock
DO_2_4 | -0.1 | 367130 | 2.4514e-05 | 0 | -0.01 | sensitivity_not_final_manufacturer_lock

## DO4_monthly_zero_stability
sensor_id | month | n_observed | negative_rate | negative_median | p01 | minimum | longest_negative_run_min | zero_equivalent_rate | zero_offset_warning_rate | severe_negative_rate
DO_1_4 | 2025-08 | 44503 | 0.31823 | -0.01 | -0.02 | -0.03 | 11 | 0.31823 | 0 | 0
DO_1_4 | 2025-09 | 42834 | 0.32925 | -0.01 | -0.02 | -0.03 | 12 | 0.32925 | 0 | 0
DO_1_4 | 2025-10 | 44625 | 0.21867 | -0.01 | -0.02 | -0.03 | 8 | 0.21867 | 0 | 0
DO_1_4 | 2025-11 | 43180 | 0.20648 | -0.01 | -0.02 | -0.03 | 10 | 0.20648 | 0 | 0
DO_1_4 | 2025-12 | 44640 | 0.30598 | -0.01 | -0.02 | -0.03 | 10 | 0.30598 | 0 | 0
DO_1_4 | 2026-01 | 44061 | 0.22203 | -0.01 | -0.02 | -0.03 | 9 | 0.22203 | 0 | 0
DO_1_4 | 2026-02 | 40320 | 0.23648 | -0.01 | -0.02 | -0.03 | 9 | 0.23648 | 0 | 0
DO_1_4 | 2026-03 | 44640 | 0.17883 | -0.01 | -0.01 | -0.03 | 8 | 0.17883 | 0 | 0
DO_1_4 | 2026-04 | 18318 | 0.27481 | -0.01 | -0.02 | -0.03 | 8 | 0.27481 | 0 | 0
DO_2_4 | 2025-08 | 44510 | 0.0002022 | -0.01 | 0.01 | -0.01 | 2 | 0.0002022 | 0 | 0
DO_2_4 | 2025-09 | 42832 | 0 |  | 0.01 | 0 | 0 | 0 | 0 | 0
DO_2_4 | 2025-10 | 44628 | 0 |  | 0.02 | 0 | 0 | 0 | 0 | 0
DO_2_4 | 2025-11 | 43180 | 0 |  | 0.04 | 0.02 | 0 | 0 | 0 | 0
DO_2_4 | 2025-12 | 44640 | 0 |  | 0.03 | 0.02 | 0 | 0 | 0 | 0
DO_2_4 | 2026-01 | 44062 | 0 |  | 0.04 | 0.02 | 0 | 0 | 0 | 0
DO_2_4 | 2026-02 | 40320 | 0 |  | 0.04 | 0.02 | 0 | 0 | 0 | 0
DO_2_4 | 2026-03 | 44640 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
DO_2_4 | 2026-04 | 18318 | 0 |  | 0.03 | 0.02 | 0 | 0 | 0 | 0

## DO4_parallel_line_diagnostic
month | n_paired | DO_1_4_median | DO_2_4_median | paired_delta_median_mg_L | paired_delta_day_block_ci_low | paired_delta_day_block_ci_high | paired_delta_n_days | paired_robust_standardized_difference | negative_jaccard | zero_equivalent_jaccard | negative_rate_DO_1_4 | negative_rate_DO_2_4 | interpretation
2025-08 | 44498 | 0 | 0.13 | -0.12 | -0.14 | -0.1 | 31 | -1.2641 | 0.00021177 | 0.00021177 | 0.31822 | 0.00020226 | parallel_line_diagnostic_not_cross_sensor_scoring
2025-09 | 42830 | 0 | 0.3 | -0.3 | -0.49 | -0.22 | 30 | -1.243 | 0 | 0 | 0.32928 | 0 | parallel_line_diagnostic_not_cross_sensor_scoring
2025-10 | 44617 | 0.01 | 0.16 | -0.13 | -0.18 | -0.1 | 31 | -1.0298 | 0 | 0 | 0.21866 | 0 | parallel_line_diagnostic_not_cross_sensor_scoring
2025-11 | 43179 | 0.01 | 0.21 | -0.17 | -0.2 | -0.125 | 30 | -1.3329 | 0 | 0 | 0.20649 | 0 | parallel_line_diagnostic_not_cross_sensor_scoring
2025-12 | 44640 | 0 | 0.06 | -0.07 | -0.07 | -0.06 | 31 | -2.9861 | 0 | 0 | 0.30598 | 0 | parallel_line_diagnostic_not_cross_sensor_scoring
2026-01 | 44061 | 0 | 0.07 | -0.07 | -0.07 | -0.06 | 31 | -2.9861 | 0 | 0 | 0.22203 | 0 | parallel_line_diagnostic_not_cross_sensor_scoring
2026-02 | 40320 | 0 | 0.08 | -0.08 | -0.09 | -0.07 | 28 | -2.4131 | 0 | 0 | 0.23648 | 0 | parallel_line_diagnostic_not_cross_sensor_scoring
2026-03 | 44640 | 0.01 | 0.09 | -0.08 | -0.1 | -0.08 | 31 | -1.8508 | 0 | 0 | 0.17883 | 0 | parallel_line_diagnostic_not_cross_sensor_scoring
2026-04 | 18318 | 0 | 0.05 | -0.05 | -0.07 | -0.05 | 13 | -3.3725 | 0 | 0 | 0.27481 | 0 | parallel_line_diagnostic_not_cross_sensor_scoring

## ORP_position_distribution
sensor_id | position | pool | n_observed | p01_mV | q25_mV | median_mV | q75_mV | p99_mV | role
ORP_1_1 | 1 | 1 | 367142 | -299.07 | -258.27 | -226.47 | -188.07 | -74.4082 | full_period_distribution_context_not_scoring_template
ORP_2_1 | 1 | 2 | 367138 | -374.23 | -236.78 | -211.67 | -174.53 | -16.6 | full_period_distribution_context_not_scoring_template
ORP_1_2 | 2 | 1 | 367137 | -400.37 | -237.77 | -163.7 | -127.63 | -51.5 | full_period_distribution_context_not_scoring_template
ORP_2_2 | 2 | 2 | 367137 | -388 | -326.73 | -286.87 | -269.97 | -226.65 | full_period_distribution_context_not_scoring_template
ORP_1_3 | 3 | 1 | 367138 | -494.33 | -291.13 | -188.17 | -111.9 | 17.63 | full_period_distribution_context_not_scoring_template
ORP_2_3 | 3 | 2 | 367140 | -477.5 | -451.87 | -431.87 | -206.03 | 32.9 | full_period_distribution_context_not_scoring_template

## ORP_parallel_position_effect
position | line_1_sensor | line_2_sensor | n_paired_minutes | n_day_blocks | median_line1_minus_line2_mV | day_block_ci_low_mV | day_block_ci_high_mV | robust_standardized_difference | role
1 | ORP_1_1 | ORP_2_1 | 367126 | 256 | -21.07 | -28.5225 | -12.0136 | -0.44457 | parallel_line_heterogeneity_diagnostic_not_scoring_template
2 | ORP_1_2 | ORP_2_2 | 367123 | 256 | 125.86 | 122.0469 | 131.3307 | 2.2028 | parallel_line_heterogeneity_diagnostic_not_scoring_template
3 | ORP_1_3 | ORP_2_3 | 367127 | 256 | 201.26 | 151.3438 | 236.0806 | 2.1025 | parallel_line_heterogeneity_diagnostic_not_scoring_template

## DO4_upper_candidate
sensor_id | split_timestamp | calibration_hours | validation_hours | calibration_median_mg_L | calibration_MAD_scale_mg_L | calibration_p99_mg_L | candidate_upper_mg_L | validation_warning_rate | validation_p99_mg_L | support_passed | status | production_role | calibration_filter | D1_source_sha256 | D2_source_sha256
DO_1_4 | 2026-01-27 04:47 | 2727 | 1329 | 0 | 0 | 0.1087 | 0.1087 | 0.0022573 | 0.0472 | TRUE | validation_candidate_support_passed | disabled_not_consumed_by_D3_score | D1_total,Q_spike,Q_step,Q_freeze,D2_Strict>=4.5 | 83207ca6f818dd309fe36cdb3adfdc9e569ea540fbca5c4acc0e45e8a321923c | ac051d9a24a17523433c63187cf63f0128efb185325a1ea789633f7fc13d04a6
DO_2_4 | 2026-01-27 04:47 | 98 | 10 | 0.3075 | 0.18162 | 1.0588 | 1.0588 | 0 | 0.6564 | FALSE | insufficient_independent_support | disabled_not_consumed_by_D3_score | D1_total,Q_spike,Q_step,Q_freeze,D2_Strict>=4.5 | 83207ca6f818dd309fe36cdb3adfdc9e569ea540fbca5c4acc0e45e8a321923c | ac051d9a24a17523433c63187cf63f0128efb185325a1ea789633f7fc13d04a6