## summary
validation | metric | value | CI_low | CI_high | n_process_time_blocks | bootstrap_unit | target | pass | required_for_acceptance | interpretation | calibration_id
unilateral_drift | ROC_AUC | 0.87979 | 0.84065 | 0.92661 | 11 | synchronized_7d_process_time_block_all_pairs | 0.7 | TRUE | TRUE | internal chronological-holdout stress test | D4CAL-V16-e615cd349a49
unilateral_step | ROC_AUC | 0.83963 | 0.79991 | 0.891 | 11 | synchronized_7d_process_time_block_all_pairs | 0.7 | TRUE | TRUE | internal chronological-holdout stress test | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC_AUC | 0.7266 | 0.68246 | 0.78548 | 11 | synchronized_7d_process_time_block_all_pairs | 0.7 | TRUE | TRUE | internal chronological-holdout stress test | D4CAL-V16-e615cd349a49
unilateral_spike | ROC_AUC | 0.55272 | 0.53792 | 0.5796 | 11 | synchronized_7d_process_time_block_all_pairs | 0.7 | FALSE | FALSE | secondary sensitivity only; isolated spikes remain a D1 responsibility | D4CAL-V16-e615cd349a49
synchronous_switch | new_false_alarm_rate | 0.031915 | 0 | 0.058267 | 11 | synchronized_7d_process_time_block_all_pairs | 0.1 | TRUE | TRUE | paired conditional FAR among windows that were non-alarming before injection | D4CAL-V16-e615cd349a49
common_mode_drift | new_false_alarm_rate | 0.031915 | 0 | 0.061748 | 11 | synchronized_7d_process_time_block_all_pairs | 0.1 | TRUE | TRUE | paired conditional FAR among windows that were non-alarming before injection | D4CAL-V16-e615cd349a49

## injection_scores
pair_id | window_id | timestamp | injection | is_unilateral_fault | anomaly_score | Q_dist | Q_trend | Q_var | Q_cp | Q_var_no_deadband | Q_dist_w1_candidate | Q_dist_ks_candidate | D4_base | D4_raw | D4_raw_full | D4_raw_w1_only | D4_raw_ks_only | risk_dist_full | risk_dist_w1 | risk_dist_ks | deadband_active | calibration_id
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | baseline | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.19773 | 0.24159 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | unilateral_drift | TRUE | 2.3625 | 2 | 3 | 4 | 3 | 4 | 2 | 2 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.87512 | 1.0835 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | unilateral_step | TRUE | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0.58 | 0.67501 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | unilateral_freeze | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 4 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.47531 | 0.5746 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | unilateral_spike | TRUE | 0.95 | 5 | 5 | 4 | 3 | 4 | 4 | 5 | 4.4 | 4.05 | 4.05 | 3.7875 | 4.05 | 0.24089 | 0.32278 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | distribution_location | TRUE | 2.5 | 1 | 5 | 4 | 3 | 4 | 1 | 2 | 3 | 2.5 | 2.5 | 2.5 | 3.0125 | 1.2862 | 1.653 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | distribution_scale | TRUE | 1.1375 | 5 | 4 | 4 | 3 | 4 | 5 | 5 | 4.15 | 3.8625 | 3.8625 | 3.8625 | 3.8625 | 0.16956 | 0.19926 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | distribution_tail | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 5 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 4.2 | 0.29031 | 0.40515 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 4 | 4 | 3.3 | 2.975 | 2.975 | 3.2375 | 3.2375 | 0.40484 | 0.42937 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | synchronous_switch | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.173 | 0.18648 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | common_mode_drift | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.173 | 0.18648 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | common_unequal | FALSE | 1.5125 | 3 | 4 | 5 | 3 | 5 | 3 | 4 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 3.75 | 0.52086 | 0.60884 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-01 | 2026-02-01 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 2 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 1.391 | 1.7905 | 0.79167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | baseline | FALSE | 1.75 | 5 | 5 | 4 | 1 | 4 | 5 | 5 | 4 | 3.25 | 3.25 | 3.25 | 3.25 | 0.10089 | 0.10334 | 0.097222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | unilateral_drift | TRUE | 3.25 | 2 | 2 | 3 | 1 | 3 | 2 | 2 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 0.89271 | 1.1036 | 0.57639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | unilateral_step | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 3 | 3 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 0.59121 | 0.67517 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | unilateral_freeze | TRUE | 2.7625 | 3 | 4 | 2 | 1 | 2 | 3 | 4 | 2.65 | 2.2375 | 2.2375 | 2.2375 | 2.5 | 0.48101 | 0.56557 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | unilateral_spike | TRUE | 1.75 | 5 | 5 | 4 | 1 | 4 | 5 | 5 | 4 | 3.25 | 3.25 | 3.25 | 3.25 | 0.22228 | 0.28251 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | distribution_location | TRUE | 2.65 | 1 | 5 | 4 | 2 | 4 | 1 | 2 | 2.8 | 2.35 | 2.35 | 2.35 | 2.8625 | 1.3511 | 1.7148 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | distribution_scale | TRUE | 2.3125 | 4 | 5 | 2 | 1 | 2 | 4 | 5 | 3.25 | 2.6875 | 2.6875 | 2.6875 | 2.95 | 0.3143 | 0.37105 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | distribution_tail | TRUE | 2.0125 | 4 | 5 | 4 | 1 | 4 | 3 | 5 | 3.65 | 2.9875 | 2.9875 | 2.725 | 3.25 | 0.35455 | 0.47518 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | distribution_mixture | TRUE | 2.575 | 3 | 5 | 2 | 1 | 2 | 3 | 4 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.47785 | 0.54179 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.051573 | 0.053547 | 0.048611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.051573 | 0.053547 | 0.048611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | common_unequal | FALSE | 2.6125 | 3 | 4 | 3 | 1 | 3 | 3 | 4 | 2.85 | 2.3875 | 2.3875 | 2.3875 | 2.65 | 0.54432 | 0.64331 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-02 | 2026-02-05 05:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.4835 | 1.9123 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | baseline | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.12795 | 0.13917 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | unilateral_drift | TRUE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.6 | 0.70665 | 0.86757 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | unilateral_step | TRUE | 2.55 | 3 | 3 | 2 | 2 | 2 | 3 | 3 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.50367 | 0.55704 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | unilateral_freeze | TRUE | 2.8125 | 2 | 3 | 2 | 2 | 2 | 2 | 3 | 2.25 | 2.1875 | 2.1875 | 2.1875 | 2.45 | 0.68734 | 0.86315 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | unilateral_spike | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.18885 | 0.24994 | 0.097222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | distribution_location | TRUE | 2.65 | 1 | 5 | 4 | 2 | 4 | 1 | 2 | 2.8 | 2.35 | 2.35 | 2.35 | 2.8625 | 1.2215 | 1.5544 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | distribution_scale | TRUE | 1.5 | 5 | 5 | 3 | 2 | 3 | 4 | 5 | 4 | 3.5 | 3.5 | 3.2375 | 3.5 | 0.24638 | 0.31341 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | distribution_tail | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 4 | 5 | 4.4 | 3.8 | 3.8 | 3.5375 | 3.8 | 0.27583 | 0.38565 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | distribution_mixture | TRUE | 2.1 | 4 | 4 | 2 | 2 | 2 | 3 | 4 | 3.2 | 2.9 | 2.9 | 2.6375 | 2.9 | 0.39972 | 0.45787 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.072484 | 0.069881 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.072484 | 0.069881 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | common_unequal | FALSE | 1.8 | 4 | 4 | 4 | 2 | 4 | 3 | 4 | 3.6 | 3.2 | 3.2 | 2.9375 | 3.2 | 0.39739 | 0.45399 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-03 | 2026-02-09 10:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 1.2333 | 1.5602 | 0.74306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | baseline | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.11992 | 0.14431 | 0.083333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | unilateral_drift | TRUE | 2.55 | 2 | 2 | 3 | 4 | 3 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.73969 | 0.8856 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | unilateral_step | TRUE | 2.5875 | 3 | 2 | 3 | 2 | 3 | 3 | 4 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.675 | 0.53963 | 0.66791 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | unilateral_freeze | TRUE | 2.325 | 2 | 4 | 2 | 4 | 2 | 2 | 4 | 2.9 | 2.675 | 2.675 | 2.675 | 3.2 | 0.66157 | 0.87577 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | unilateral_spike | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.18541 | 0.24884 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 4 | 5 | 4 | 1 | 2 | 3.4 | 2.8 | 2.8 | 2.8 | 3.3125 | 1.2401 | 1.6131 | 0.68056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | distribution_scale | TRUE | 0.8125 | 4 | 5 | 4 | 4 | 4 | 4 | 5 | 4.25 | 4.1875 | 4.1875 | 4.1875 | 4.45 | 0.28624 | 0.3567 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | distribution_tail | TRUE | 0.6625 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 4.45 | 4.3375 | 4.3375 | 4.3375 | 4.6 | 0.29366 | 0.4061 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | distribution_mixture | TRUE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.42346 | 0.46039 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | synchronous_switch | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.092612 | 0.084909 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | common_mode_drift | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.092612 | 0.084909 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | common_unequal | FALSE | 1.85 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 3.2 | 3.15 | 3.15 | 3.15 | 3.4125 | 0.42038 | 0.49693 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-04 | 2026-02-13 15:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 2.1625 | 1.2149 | 1.5017 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | baseline | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.16798 | 0.17348 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | unilateral_drift | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0.86422 | 1.0654 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | unilateral_step | TRUE | 2.8125 | 2 | 3 | 2 | 2 | 2 | 2 | 3 | 2.25 | 2.1875 | 2.1875 | 2.1875 | 2.45 | 0.62534 | 0.71353 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | unilateral_freeze | TRUE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.35 | 0.43551 | 0.50825 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | unilateral_spike | TRUE | 1.6125 | 4 | 5 | 4 | 2 | 4 | 4 | 5 | 3.85 | 3.3875 | 3.3875 | 3.3875 | 3.65 | 0.31381 | 0.41653 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | distribution_location | TRUE | 2.35 | 1 | 5 | 4 | 4 | 4 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.3973 | 1.7825 | 0.81944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | distribution_scale | TRUE | 1.9125 | 4 | 5 | 2 | 2 | 2 | 3 | 4 | 3.45 | 3.0875 | 3.0875 | 2.825 | 3.0875 | 0.38308 | 0.46254 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | distribution_tail | TRUE | 2.025 | 3 | 5 | 3 | 2 | 3 | 3 | 5 | 3.3 | 2.975 | 2.975 | 2.975 | 3.5 | 0.40548 | 0.56006 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 3 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.51279 | 0.57687 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.063536 | 0.059597 | 0.069444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.063536 | 0.059597 | 0.069444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | common_unequal | FALSE | 2.2125 | 3 | 4 | 3 | 2 | 3 | 3 | 4 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.05 | 0.50025 | 0.57449 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-05 | 2026-02-17 20:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 4 | 1 | 4 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.3815 | 1.71 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | baseline | FALSE | 1.95 | 4 | 4 | 3 | 2 | 3 | 4 | 4 | 3.4 | 3.05 | 3.05 | 3.05 | 3.05 | 0.34421 | 0.37461 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | unilateral_drift | TRUE | 3.4375 | 2 | 1 | 2 | 2 | 2 | 2 | 2 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.5625 | 0.95863 | 1.1903 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | unilateral_step | TRUE | 3.4375 | 2 | 1 | 2 | 2 | 2 | 2 | 2 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.5625 | 0.72078 | 0.84944 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | unilateral_freeze | TRUE | 1.9125 | 4 | 5 | 2 | 2 | 2 | 4 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.36453 | 0.40385 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | unilateral_spike | TRUE | 2.2125 | 3 | 4 | 3 | 2 | 3 | 3 | 4 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.05 | 0.47256 | 0.59316 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | distribution_location | TRUE | 2.9875 | 1 | 4 | 3 | 2 | 3 | 1 | 2 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.525 | 1.4272 | 1.8648 | 0.77083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | distribution_scale | TRUE | 2.55 | 3 | 3 | 2 | 2 | 2 | 3 | 4 | 2.6 | 2.45 | 2.45 | 2.45 | 2.7125 | 0.54232 | 0.66312 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | distribution_tail | TRUE | 2.2125 | 3 | 4 | 3 | 2 | 3 | 2 | 4 | 3.05 | 2.7875 | 2.7875 | 2.525 | 3.05 | 0.56881 | 0.76283 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | distribution_mixture | TRUE | 2.55 | 3 | 3 | 2 | 2 | 2 | 3 | 4 | 2.6 | 2.45 | 2.45 | 2.45 | 2.7125 | 0.55578 | 0.66705 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | synchronous_switch | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.20299 | 0.23183 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | common_mode_drift | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.20299 | 0.23183 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | common_unequal | FALSE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2.2625 | 0.63393 | 0.751 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-06 | 2026-02-22 01:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 1.3096 | 1.6919 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | baseline | FALSE | 1.575 | 5 | 3 | 5 | 2 | 5 | 5 | 5 | 3.9 | 3.425 | 3.425 | 3.425 | 3.425 | 0.094542 | 0.11127 | 0.069444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | unilateral_drift | TRUE | 2.025 | 2 | 4 | 4 | 4 | 4 | 2 | 2 | 3.3 | 2.975 | 2.975 | 2.975 | 2.975 | 0.89418 | 1.1153 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | unilateral_step | TRUE | 2.4 | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 2.8 | 2.6 | 2.6 | 2.3375 | 2.6 | 0.61108 | 0.72217 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | unilateral_freeze | TRUE | 2.1 | 4 | 4 | 2 | 2 | 2 | 4 | 4 | 3.2 | 2.9 | 2.9 | 2.9 | 2.9 | 0.30563 | 0.33345 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | unilateral_spike | TRUE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 5 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.6125 | 0.19415 | 0.27266 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | distribution_location | TRUE | 2.425 | 1 | 3 | 5 | 5 | 5 | 1 | 2 | 3.1 | 2.575 | 2.575 | 2.575 | 3.0875 | 1.1965 | 1.5081 | 0.72917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | distribution_scale | TRUE | 1.95 | 4 | 4 | 3 | 2 | 3 | 3 | 5 | 3.4 | 3.05 | 3.05 | 2.7875 | 3.3125 | 0.34577 | 0.44203 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | distribution_tail | TRUE | 1.8375 | 4 | 3 | 5 | 2 | 5 | 3 | 5 | 3.55 | 3.1625 | 3.1625 | 2.9 | 3.425 | 0.31996 | 0.44993 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 4 | 3.1 | 2.825 | 2.825 | 2.825 | 3.0875 | 0.4643 | 0.52384 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | synchronous_switch | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.11309 | 0.12829 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | common_mode_drift | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.11309 | 0.12829 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | common_unequal | FALSE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.50488 | 0.60536 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-07 | 2026-02-26 07:00 | opposite_direction | FALSE | 2.8 | 1 | 1 | 5 | 5 | 5 | 1 | 2 | 2.6 | 2.2 | 2.2 | 2.2 | 2.4625 | 1.5678 | 2.0759 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | baseline | FALSE | 2.5375 | 4 | 3 | 3 | 1 | 3 | 3 | 5 | 2.95 | 2.4625 | 2.4625 | 2.2 | 2.725 | 0.38736 | 0.50207 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | unilateral_drift | TRUE | 2.8125 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2.25 | 2.1875 | 2.1875 | 2.1875 | 2.1875 | 0.92985 | 1.1562 | 0.59028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | unilateral_step | TRUE | 2.8125 | 2 | 3 | 2 | 2 | 2 | 2 | 3 | 2.25 | 2.1875 | 2.1875 | 2.1875 | 2.45 | 0.70362 | 0.83011 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | unilateral_freeze | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 2 | 4 | 2.4 | 2.05 | 2.05 | 1.7875 | 2.3125 | 0.61052 | 0.76291 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | unilateral_spike | TRUE | 2.8 | 3 | 3 | 3 | 1 | 3 | 3 | 5 | 2.6 | 2.2 | 2.2 | 2.2 | 2.725 | 0.43088 | 0.56999 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | distribution_location | TRUE | 3.175 | 1 | 3 | 3 | 2 | 3 | 1 | 2 | 2.1 | 1.825 | 1.825 | 1.825 | 2.3375 | 1.3759 | 1.7793 | 0.77083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | distribution_scale | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 3 | 4 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 0.47831 | 0.59349 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | distribution_tail | TRUE | 2.7625 | 3 | 4 | 2 | 1 | 2 | 3 | 5 | 2.65 | 2.2375 | 2.2375 | 2.2375 | 2.7625 | 0.42536 | 0.58393 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | distribution_mixture | TRUE | 2.725 | 3 | 5 | 1 | 1 | 1 | 3 | 3 | 2.7 | 2.275 | 2.275 | 2.275 | 2.275 | 0.5761 | 0.64535 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | synchronous_switch | FALSE | 0.4375 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 4.75 | 4.5625 | 4.5625 | 4.5625 | 4.5625 | 0.17831 | 0.24163 | 0.083333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | common_mode_drift | FALSE | 0.4375 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 4.75 | 4.5625 | 4.5625 | 4.5625 | 4.5625 | 0.17831 | 0.24163 | 0.083333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | common_unequal | FALSE | 1.325 | 3 | 5 | 3 | 5 | 3 | 3 | 4 | 3.9 | 3.675 | 3.675 | 3.675 | 3.9375 | 0.54529 | 0.65419 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-08 | 2026-03-02 12:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.4443 | 1.8563 | 0.82639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | baseline | FALSE | 1.9 | 5 | 5 | 3 | 1 | 3 | 5 | 5 | 3.8 | 3.1 | 3.1 | 3.1 | 3.1 | 0.22607 | 0.26568 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | unilateral_drift | TRUE | 3.4375 | 2 | 1 | 2 | 2 | 2 | 2 | 2 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.5625 | 1.0915 | 1.3608 | 0.6875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | unilateral_step | TRUE | 3.4 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 0.79659 | 0.94803 | 0.56944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | unilateral_freeze | TRUE | 2.55 | 3 | 3 | 2 | 2 | 2 | 3 | 3 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.51818 | 0.54883 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | unilateral_spike | TRUE | 2.425 | 3 | 5 | 3 | 1 | 3 | 3 | 5 | 3.1 | 2.575 | 2.575 | 2.575 | 3.1 | 0.40371 | 0.53396 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | distribution_location | TRUE | 2.8 | 1 | 5 | 3 | 2 | 3 | 1 | 1 | 2.6 | 2.2 | 2.2 | 2.2 | 2.2 | 1.5451 | 2.0289 | 0.81944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | distribution_scale | TRUE | 2.575 | 3 | 5 | 2 | 1 | 2 | 3 | 5 | 2.9 | 2.425 | 2.425 | 2.425 | 2.95 | 0.43827 | 0.57767 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | distribution_tail | TRUE | 2.425 | 3 | 5 | 3 | 1 | 3 | 3 | 5 | 3.1 | 2.575 | 2.575 | 2.575 | 3.1 | 0.47525 | 0.63005 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | distribution_mixture | TRUE | 2.7625 | 3 | 4 | 2 | 1 | 2 | 3 | 3 | 2.65 | 2.2375 | 2.2375 | 2.2375 | 2.2375 | 0.52693 | 0.60507 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | synchronous_switch | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.17172 | 0.19361 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | common_mode_drift | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.17172 | 0.19361 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | common_unequal | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.6 | 0.69443 | 0.81943 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-09 | 2026-03-06 17:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 1.3532 | 1.7136 | 0.8125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | baseline | FALSE | 1.725 | 5 | 3 | 4 | 2 | 4 | 5 | 5 | 3.7 | 3.275 | 3.275 | 3.275 | 3.275 | 0.16974 | 0.18105 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | unilateral_drift | TRUE | 2.875 | 2 | 4 | 3 | 1 | 3 | 2 | 2 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 0.79808 | 0.96439 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | unilateral_step | TRUE | 2.7625 | 3 | 4 | 2 | 1 | 2 | 3 | 3 | 2.65 | 2.2375 | 2.2375 | 2.2375 | 2.2375 | 0.55136 | 0.64116 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | unilateral_freeze | TRUE | 2.7375 | 3 | 2 | 2 | 2 | 2 | 2 | 4 | 2.35 | 2.2625 | 2.2625 | 2 | 2.525 | 0.56179 | 0.75113 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | unilateral_spike | TRUE | 1.725 | 5 | 3 | 4 | 2 | 4 | 4 | 5 | 3.7 | 3.275 | 3.275 | 3.0125 | 3.275 | 0.26686 | 0.32903 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | distribution_location | TRUE | 3.025 | 1 | 3 | 4 | 2 | 4 | 1 | 2 | 2.3 | 1.975 | 1.975 | 1.975 | 2.4875 | 1.3663 | 1.7725 | 0.75694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | distribution_scale | TRUE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.19505 | 0.24638 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | distribution_tail | TRUE | 2.3875 | 4 | 3 | 4 | 1 | 4 | 3 | 5 | 3.15 | 2.6125 | 2.6125 | 2.35 | 2.875 | 0.37509 | 0.51405 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | distribution_mixture | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 3 | 4 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 0.42045 | 0.46927 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | synchronous_switch | FALSE | 1.7875 | 5 | 4 | 5 | 1 | 5 | 5 | 5 | 3.95 | 3.2125 | 3.2125 | 3.2125 | 3.2125 | 0.15438 | 0.15545 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | common_mode_drift | FALSE | 1.7875 | 5 | 4 | 5 | 1 | 5 | 5 | 5 | 3.95 | 3.2125 | 3.2125 | 3.2125 | 3.2125 | 0.15438 | 0.15545 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | common_unequal | FALSE | 2.275 | 3 | 5 | 4 | 1 | 4 | 3 | 4 | 3.3 | 2.725 | 2.725 | 2.725 | 2.9875 | 0.44297 | 0.52995 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-10 | 2026-03-10 22:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 3 | 2 | 3 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.5666 | 1.9953 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | baseline | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.21347 | 0.26319 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | unilateral_drift | TRUE | 2.25 | 2 | 2 | 5 | 4 | 5 | 2 | 2 | 3 | 2.75 | 2.75 | 2.75 | 2.75 | 0.82423 | 1.0126 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | unilateral_step | TRUE | 1.85 | 3 | 3 | 3 | 4 | 3 | 3 | 3 | 3.2 | 3.15 | 3.15 | 3.15 | 3.15 | 0.51896 | 0.59179 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | unilateral_freeze | TRUE | 2.0625 | 3 | 4 | 2 | 4 | 2 | 3 | 4 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 3.2 | 0.45502 | 0.54077 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | unilateral_spike | TRUE | 0.6625 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 4.45 | 4.3375 | 4.3375 | 4.3375 | 4.6 | 0.29754 | 0.4172 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | distribution_location | TRUE | 1.8375 | 2 | 5 | 4 | 4 | 4 | 1 | 2 | 3.55 | 3.1625 | 3.1625 | 2.65 | 3.1625 | 1.093 | 1.4142 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | distribution_scale | TRUE | 1 | 4 | 4 | 4 | 4 | 4 | 3 | 5 | 4 | 4 | 4 | 3.4875 | 4.2625 | 0.35824 | 0.45817 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | distribution_tail | TRUE | 0.6625 | 4 | 5 | 5 | 4 | 5 | 4 | 5 | 4.45 | 4.3375 | 4.3375 | 4.3375 | 4.6 | 0.31179 | 0.43168 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | distribution_mixture | TRUE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.44914 | 0.48467 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.17502 | 0.19911 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.17502 | 0.19911 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | common_unequal | FALSE | 1.5125 | 3 | 4 | 4 | 4 | 4 | 3 | 4 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 4 | 0.48525 | 0.56338 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-11 | 2026-03-15 03:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 3 | 4 | 3 | 1 | 2 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 1.2725 | 1.6301 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | baseline | FALSE | 2.125 | 5 | 3 | 4 | 1 | 4 | 5 | 5 | 3.5 | 2.875 | 2.875 | 2.875 | 2.875 | 0.1608 | 0.19392 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | unilateral_drift | TRUE | 2.3625 | 2 | 3 | 4 | 3 | 4 | 2 | 2 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 1.0111 | 1.2777 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | unilateral_step | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 2 | 3 | 2.4 | 2.05 | 2.05 | 1.7875 | 2.05 | 0.60247 | 0.72171 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | unilateral_freeze | TRUE | 2.7625 | 3 | 4 | 2 | 1 | 2 | 3 | 4 | 2.65 | 2.2375 | 2.2375 | 2.2375 | 2.5 | 0.4277 | 0.54154 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | unilateral_spike | TRUE | 2.2 | 4 | 4 | 4 | 1 | 4 | 4 | 5 | 3.4 | 2.8 | 2.8 | 2.8 | 3.0625 | 0.30084 | 0.41807 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | distribution_location | TRUE | 2.875 | 1 | 3 | 4 | 3 | 4 | 1 | 2 | 2.5 | 2.125 | 2.125 | 2.125 | 2.6375 | 1.2833 | 1.662 | 0.71528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | distribution_scale | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 3 | 5 | 2.4 | 2.05 | 2.05 | 2.05 | 2.575 | 0.41413 | 0.54207 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | distribution_tail | TRUE | 2.4625 | 3 | 4 | 4 | 1 | 4 | 3 | 5 | 3.05 | 2.5375 | 2.5375 | 2.5375 | 3.0625 | 0.40767 | 0.58222 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | distribution_mixture | TRUE | 2.575 | 3 | 5 | 2 | 1 | 2 | 3 | 4 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.46027 | 0.53563 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | synchronous_switch | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.069595 | 0.078954 | 0.055556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | common_mode_drift | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.069595 | 0.078954 | 0.055556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | common_unequal | FALSE | 1.475 | 3 | 5 | 4 | 3 | 4 | 2 | 4 | 3.7 | 3.525 | 3.525 | 3.0125 | 3.7875 | 0.59208 | 0.74607 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-12 | 2026-03-19 08:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.4823 | 1.9196 | 0.82639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | baseline | FALSE | 3.1 | 2 | 2 | 4 | 1 | 4 | 2 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 0.98065 | 1.2224 | 0.61806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | unilateral_drift | TRUE | 2.6125 | 4 | 1 | 3 | 3 | 3 | 4 | 5 | 2.85 | 2.3875 | 2.3875 | 2.3875 | 2.65 | 0.29756 | 0.34315 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | unilateral_step | TRUE | 2.9125 | 4 | 1 | 3 | 1 | 3 | 4 | 5 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.35 | 0.36124 | 0.43541 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | unilateral_freeze | TRUE | 3.55 | 1 | 1 | 2 | 3 | 2 | 1 | 2 | 1.6 | 1.45 | 1.45 | 1.45 | 1.7125 | 1.6195 | 2.2178 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | unilateral_spike | TRUE | 2.55 | 2 | 2 | 4 | 3 | 4 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.99249 | 1.2653 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | distribution_location | TRUE | 2.2875 | 3 | 2 | 4 | 3 | 4 | 3 | 5 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 3.2375 | 0.43019 | 0.55495 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | distribution_scale | TRUE | 3.1 | 2 | 2 | 4 | 1 | 4 | 2 | 3 | 2.2 | 1.9 | 1.9 | 1.9 | 2.1625 | 0.89241 | 1.1772 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | distribution_tail | TRUE | 3.1 | 2 | 2 | 4 | 1 | 4 | 2 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 0.97529 | 1.2597 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | distribution_mixture | TRUE | 3.1375 | 3 | 2 | 2 | 1 | 2 | 3 | 3 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 1.8625 | 0.51544 | 0.57203 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | synchronous_switch | FALSE | 2.3625 | 2 | 3 | 3 | 4 | 3 | 2 | 2 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.76514 | 0.91413 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | common_mode_drift | FALSE | 2.3625 | 2 | 3 | 3 | 4 | 3 | 2 | 2 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.76514 | 0.91413 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | common_unequal | FALSE | 2.875 | 3 | 1 | 3 | 3 | 3 | 3 | 4 | 2.5 | 2.125 | 2.125 | 2.125 | 2.3875 | 0.48961 | 0.61231 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-13 | 2026-03-23 14:00 | opposite_direction | FALSE | 3.1375 | 2 | 1 | 4 | 2 | 4 | 2 | 4 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.3875 | 0.62733 | 0.77703 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | baseline | FALSE | 1.9375 | 5 | 4 | 4 | 1 | 4 | 5 | 5 | 3.75 | 3.0625 | 3.0625 | 3.0625 | 3.0625 | 0.16683 | 0.18546 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | unilateral_drift | TRUE | 3.1375 | 2 | 1 | 3 | 3 | 3 | 2 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 1.8625 | 1.031 | 1.3295 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | unilateral_step | TRUE | 3.4 | 2 | 2 | 2 | 1 | 2 | 2 | 3 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 0.63804 | 0.76248 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | unilateral_freeze | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 3 | 4 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 0.43858 | 0.50874 | 0.33333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | unilateral_spike | TRUE | 2.0125 | 4 | 5 | 4 | 1 | 4 | 4 | 5 | 3.65 | 2.9875 | 2.9875 | 2.9875 | 3.25 | 0.30903 | 0.42246 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | distribution_location | TRUE | 2.6875 | 1 | 4 | 4 | 3 | 4 | 1 | 2 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.825 | 1.3173 | 1.7233 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | distribution_scale | TRUE | 2.575 | 3 | 5 | 2 | 1 | 2 | 3 | 4 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.4315 | 0.53399 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | distribution_tail | TRUE | 2.35 | 4 | 4 | 3 | 1 | 3 | 3 | 5 | 3.2 | 2.65 | 2.65 | 2.3875 | 2.9125 | 0.37496 | 0.50919 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | distribution_mixture | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 3 | 4 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 0.49001 | 0.56669 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.23407 | 0.26049 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.23407 | 0.26049 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | common_unequal | FALSE | 2.7 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 2.4 | 2.3 | 2.3 | 2.3 | 2.5625 | 0.6499 | 0.79613 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-14 | 2026-03-27 19:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 3 | 2 | 3 | 1 | 2 | 1.6 | 1.45 | 1.45 | 1.45 | 1.7125 | 1.3142 | 1.6487 | 0.8125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | baseline | FALSE | 1.025 | 5 | 3 | 4 | 5 | 4 | 5 | 5 | 4.3 | 3.975 | 3.975 | 3.975 | 3.975 | 0.21747 | 0.27449 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | unilateral_drift | TRUE | 2.2125 | 2 | 3 | 3 | 5 | 3 | 2 | 2 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 2.7875 | 1.0618 | 1.3253 | 0.66667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | unilateral_step | TRUE | 2.175 | 2 | 4 | 2 | 5 | 2 | 2 | 2 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.80395 | 0.94177 | 0.59722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | unilateral_freeze | TRUE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.35 | 0.52155 | 0.60999 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | unilateral_spike | TRUE | 1.2875 | 4 | 3 | 4 | 5 | 4 | 3 | 5 | 3.95 | 3.7125 | 3.7125 | 3.45 | 3.975 | 0.34594 | 0.47934 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | distribution_location | TRUE | 2.575 | 1 | 3 | 4 | 5 | 4 | 1 | 2 | 2.9 | 2.425 | 2.425 | 2.425 | 2.9375 | 1.4342 | 1.8671 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | distribution_scale | TRUE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 5 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.6125 | 0.45461 | 0.60027 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | distribution_tail | TRUE | 1.7 | 3 | 3 | 3 | 5 | 3 | 3 | 5 | 3.4 | 3.3 | 3.3 | 3.3 | 3.825 | 0.45696 | 0.61809 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | distribution_mixture | TRUE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 3 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.57742 | 0.64756 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.13798 | 0.15127 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.13798 | 0.15127 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | common_unequal | FALSE | 1.6875 | 2 | 5 | 4 | 5 | 4 | 2 | 3 | 3.75 | 3.3125 | 3.3125 | 3.3125 | 3.825 | 0.63565 | 0.73997 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-15 | 2026-04-01 | opposite_direction | FALSE | 2.8 | 1 | 1 | 5 | 5 | 5 | 1 | 1 | 2.6 | 2.2 | 2.2 | 2.2 | 2.2 | 1.5722 | 2.0371 | 0.875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | baseline | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.1576 | 0.17934 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | unilateral_drift | TRUE | 3.2875 | 2 | 1 | 3 | 2 | 3 | 2 | 2 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.7125 | 0.9189 | 1.1472 | 0.57639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | unilateral_step | TRUE | 3.175 | 3 | 1 | 2 | 2 | 2 | 3 | 3 | 2.1 | 1.825 | 1.825 | 1.825 | 1.825 | 0.60612 | 0.70001 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | unilateral_freeze | TRUE | 2.7375 | 3 | 2 | 2 | 2 | 2 | 3 | 4 | 2.35 | 2.2625 | 2.2625 | 2.2625 | 2.525 | 0.42353 | 0.52069 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | unilateral_spike | TRUE | 1.8 | 4 | 4 | 4 | 2 | 4 | 4 | 5 | 3.6 | 3.2 | 3.2 | 3.2 | 3.4625 | 0.2913 | 0.37902 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | distribution_location | TRUE | 2.8375 | 1 | 4 | 4 | 2 | 4 | 1 | 2 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.675 | 1.2484 | 1.5945 | 0.72917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | distribution_scale | TRUE | 1.9125 | 4 | 5 | 2 | 2 | 2 | 4 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.35894 | 0.41767 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | distribution_tail | TRUE | 1.8 | 4 | 4 | 4 | 2 | 4 | 3 | 5 | 3.6 | 3.2 | 3.2 | 2.9375 | 3.4625 | 0.33299 | 0.45776 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 4 | 3.1 | 2.825 | 2.825 | 2.825 | 3.0875 | 0.47942 | 0.53977 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.16218 | 0.1916 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.16218 | 0.1916 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | common_unequal | FALSE | 2.5875 | 3 | 2 | 3 | 2 | 3 | 3 | 3 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.4125 | 0.57752 | 0.68475 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-16 | 2026-04-05 05:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 2.1625 | 1.3335 | 1.7041 | 0.77778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | baseline | FALSE | 1.4625 | 5 | 2 | 4 | 5 | 4 | 4 | 5 | 4.05 | 3.5375 | 3.5375 | 3.275 | 3.5375 | 0.24683 | 0.32805 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | unilateral_drift | TRUE | 3.4375 | 2 | 1 | 3 | 1 | 3 | 2 | 2 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.5625 | 0.93187 | 1.1642 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | unilateral_step | TRUE | 3.5875 | 2 | 1 | 2 | 1 | 2 | 2 | 3 | 1.55 | 1.4125 | 1.4125 | 1.4125 | 1.675 | 0.65136 | 0.77541 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | unilateral_freeze | TRUE | 2.2875 | 3 | 2 | 2 | 5 | 2 | 3 | 3 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.7125 | 0.50785 | 0.55938 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | unilateral_spike | TRUE | 1.725 | 4 | 2 | 4 | 5 | 4 | 4 | 5 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.29906 | 0.41511 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | distribution_location | TRUE | 3.0625 | 1 | 2 | 4 | 3 | 4 | 1 | 2 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 2.45 | 1.5115 | 2.0007 | 0.77778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | distribution_scale | TRUE | 1.875 | 4 | 2 | 3 | 5 | 3 | 4 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.34886 | 0.43328 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | distribution_tail | TRUE | 1.9875 | 3 | 2 | 4 | 5 | 4 | 3 | 5 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.5375 | 0.48933 | 0.68593 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | distribution_mixture | TRUE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.35 | 0.46264 | 0.50718 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | synchronous_switch | FALSE | 1.875 | 5 | 3 | 3 | 2 | 3 | 5 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.125 | 0.26795 | 0.28454 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | common_mode_drift | FALSE | 1.875 | 5 | 3 | 3 | 2 | 3 | 5 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.125 | 0.26795 | 0.28454 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | common_unequal | FALSE | 3.4375 | 2 | 1 | 3 | 1 | 3 | 2 | 3 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.825 | 0.63479 | 0.76632 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-17 | 2026-04-09 10:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 4 | 1 | 4 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.289 | 1.602 | 0.81944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | baseline | FALSE | 1.875 | 3 | 5 | 4 | 2 | 4 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.43114 | 0.53802 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | unilateral_drift | TRUE | 2.85 | 2 | 2 | 3 | 2 | 3 | 2 | 2 | 2.2 | 2.15 | 2.15 | 2.15 | 2.15 | 0.88501 | 1.0815 | 0.59028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | unilateral_step | TRUE | 2.85 | 2 | 2 | 3 | 2 | 3 | 3 | 3 | 2.2 | 2.15 | 2.15 | 2.4125 | 2.4125 | 0.61835 | 0.69725 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | unilateral_freeze | TRUE | 2.625 | 2 | 4 | 2 | 2 | 2 | 2 | 3 | 2.5 | 2.375 | 2.375 | 2.375 | 2.6375 | 0.90806 | 1.1801 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | unilateral_spike | TRUE | 1.875 | 3 | 5 | 4 | 2 | 4 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.44481 | 0.56079 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | distribution_location | TRUE | 2.65 | 1 | 5 | 4 | 2 | 4 | 1 | 2 | 2.8 | 2.35 | 2.35 | 2.35 | 2.8625 | 1.2619 | 1.6077 | 0.74306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | distribution_scale | TRUE | 1.7625 | 4 | 5 | 3 | 2 | 3 | 4 | 5 | 3.65 | 3.2375 | 3.2375 | 3.2375 | 3.5 | 0.33275 | 0.39717 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | distribution_tail | TRUE | 1.6125 | 4 | 5 | 4 | 2 | 4 | 4 | 4 | 3.85 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 0.38234 | 0.42891 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 4 | 3.1 | 2.825 | 2.825 | 2.825 | 3.0875 | 0.41348 | 0.43914 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | synchronous_switch | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 4 | 5 | 4.2 | 3.65 | 3.65 | 3.3875 | 3.65 | 0.27519 | 0.31049 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | common_mode_drift | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 4 | 5 | 4.2 | 3.65 | 3.65 | 3.3875 | 3.65 | 0.27519 | 0.31049 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | common_unequal | FALSE | 2.5125 | 2 | 3 | 4 | 2 | 4 | 2 | 3 | 2.65 | 2.4875 | 2.4875 | 2.4875 | 2.75 | 0.65084 | 0.74677 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO11 | PAIR_DO11-18 | 2026-04-13 16:00 | opposite_direction | FALSE | 3.2875 | 2 | 1 | 3 | 2 | 3 | 1 | 2 | 1.95 | 1.7125 | 1.7125 | 1.45 | 1.7125 | 1.1313 | 1.4086 | 0.71528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | baseline | FALSE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.18763 | 0.2155 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | unilateral_drift | TRUE | 2.4 | 2 | 2 | 3 | 5 | 3 | 2 | 2 | 2.8 | 2.6 | 2.6 | 2.6 | 2.6 | 0.78867 | 0.94871 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | unilateral_step | TRUE | 2.2875 | 3 | 2 | 2 | 5 | 2 | 3 | 3 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.7125 | 0.55566 | 0.60202 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | unilateral_freeze | TRUE | 2.3625 | 2 | 3 | 2 | 5 | 2 | 2 | 3 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.9 | 0.72815 | 0.88025 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | unilateral_spike | TRUE | 0.85 | 4 | 4 | 4 | 5 | 4 | 3 | 5 | 4.2 | 4.15 | 4.15 | 3.6375 | 4.4125 | 0.32872 | 0.44138 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | distribution_location | TRUE | 2.3875 | 1 | 4 | 4 | 5 | 4 | 1 | 2 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 3.125 | 1.2258 | 1.5615 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | distribution_scale | TRUE | 1.8375 | 4 | 3 | 2 | 5 | 2 | 3 | 5 | 3.55 | 3.1625 | 3.1625 | 2.9 | 3.425 | 0.37598 | 0.47386 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | distribution_tail | TRUE | 1.25 | 4 | 4 | 3 | 5 | 3 | 3 | 5 | 4 | 3.75 | 3.75 | 3.4875 | 4.0125 | 0.36782 | 0.49728 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | distribution_mixture | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.50852 | 0.58365 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.13413 | 0.13558 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.13413 | 0.13558 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | common_unequal | FALSE | 1.55 | 3 | 3 | 4 | 5 | 4 | 3 | 4 | 3.6 | 3.45 | 3.45 | 3.45 | 3.7125 | 0.41628 | 0.49472 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-01 | 2026-02-01 | opposite_direction | FALSE | 2.95 | 1 | 1 | 4 | 5 | 4 | 1 | 2 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 1.3636 | 1.7356 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | baseline | FALSE | 0.7375 | 5 | 4 | 4 | 4 | 4 | 5 | 5 | 4.35 | 4.2625 | 4.2625 | 4.2625 | 4.2625 | 0.18688 | 0.18647 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | unilateral_drift | TRUE | 2.2125 | 2 | 3 | 4 | 4 | 4 | 2 | 2 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 2.7875 | 0.95502 | 1.1426 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | unilateral_step | TRUE | 2.625 | 2 | 4 | 2 | 2 | 2 | 3 | 2 | 2.5 | 2.375 | 2.375 | 2.6375 | 2.375 | 0.63387 | 0.69997 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | unilateral_freeze | TRUE | 2.8375 | 3 | 2 | 1 | 4 | 1 | 3 | 4 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.425 | 0.5385 | 0.64287 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | unilateral_spike | TRUE | 1 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 4 | 4.2625 | 0.31501 | 0.40465 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | distribution_location | TRUE | 2.3875 | 1 | 4 | 4 | 5 | 4 | 1 | 1 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 1.519 | 1.9392 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | distribution_scale | TRUE | 0.7375 | 5 | 4 | 4 | 4 | 4 | 5 | 5 | 4.35 | 4.2625 | 4.2625 | 4.2625 | 4.2625 | 0.22164 | 0.25366 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | distribution_tail | TRUE | 1.7 | 3 | 3 | 4 | 4 | 4 | 3 | 5 | 3.4 | 3.3 | 3.3 | 3.3 | 3.825 | 0.43265 | 0.58682 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | distribution_mixture | TRUE | 2.25 | 3 | 3 | 2 | 4 | 2 | 3 | 3 | 3 | 2.75 | 2.75 | 2.75 | 2.75 | 0.46252 | 0.48846 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.13693 | 0.14026 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.13693 | 0.14026 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | common_unequal | FALSE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 3 | 3.7 | 3.275 | 3.275 | 3.275 | 3.275 | 0.5927 | 0.65449 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-02 | 2026-02-05 05:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 3 | 4 | 3 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.8212 | 2.4427 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | baseline | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.12456 | 0.13815 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | unilateral_drift | TRUE | 2.3625 | 2 | 3 | 3 | 4 | 3 | 2 | 2 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.80999 | 0.98887 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | unilateral_step | TRUE | 2.25 | 3 | 3 | 2 | 4 | 2 | 3 | 3 | 3 | 2.75 | 2.75 | 2.75 | 2.75 | 0.58682 | 0.6447 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | unilateral_freeze | TRUE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.56076 | 0.69385 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | unilateral_spike | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.18511 | 0.25758 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 2 | 3.4 | 2.8 | 2.8 | 2.8 | 3.3125 | 1.2592 | 1.6126 | 0.72917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | distribution_scale | TRUE | 0.95 | 5 | 5 | 3 | 4 | 3 | 4 | 5 | 4.4 | 4.05 | 4.05 | 3.7875 | 4.05 | 0.23531 | 0.30886 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | distribution_tail | TRUE | 0.6625 | 4 | 5 | 5 | 4 | 5 | 3 | 5 | 4.45 | 4.3375 | 4.3375 | 3.825 | 4.6 | 0.32434 | 0.46186 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | distribution_mixture | TRUE | 1.6125 | 4 | 5 | 2 | 4 | 2 | 4 | 4 | 3.85 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 0.39133 | 0.43463 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | synchronous_switch | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.084057 | 0.07991 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | common_mode_drift | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.084057 | 0.07991 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | common_unequal | FALSE | 1.5125 | 3 | 4 | 4 | 4 | 4 | 3 | 4 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 4 | 0.49335 | 0.55373 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-03 | 2026-02-09 10:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 5 | 4 | 5 | 1 | 2 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 1.2305 | 1.5601 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | baseline | FALSE | 1.1 | 5 | 5 | 3 | 3 | 3 | 4 | 5 | 4.2 | 3.9 | 3.9 | 3.6375 | 3.9 | 0.25506 | 0.3001 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | unilateral_drift | TRUE | 2.55 | 2 | 2 | 4 | 3 | 4 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.89572 | 1.0994 | 0.59028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | unilateral_step | TRUE | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0.57835 | 0.67224 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | unilateral_freeze | TRUE | 2.6875 | 2 | 5 | 1 | 3 | 1 | 2 | 4 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.8375 | 0.64869 | 0.87281 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | unilateral_spike | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 4 | 5 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 3.9 | 0.3252 | 0.42163 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | distribution_location | TRUE | 2.65 | 1 | 5 | 3 | 3 | 3 | 1 | 2 | 2.8 | 2.35 | 2.35 | 2.35 | 2.8625 | 1.4232 | 1.835 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.090822 | 0.10044 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | distribution_tail | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 3 | 5 | 3.85 | 3.6375 | 3.6375 | 3.375 | 3.9 | 0.38088 | 0.54684 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 4 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.44302 | 0.47447 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | synchronous_switch | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.17993 | 0.18877 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | common_mode_drift | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.17993 | 0.18877 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | common_unequal | FALSE | 1.5125 | 3 | 4 | 5 | 3 | 5 | 3 | 4 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 3.75 | 0.5213 | 0.6142 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-04 | 2026-02-13 15:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.63 | 2.1149 | 0.90278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | baseline | FALSE | 2.7375 | 3 | 2 | 2 | 2 | 2 | 3 | 4 | 2.35 | 2.2625 | 2.2625 | 2.2625 | 2.525 | 0.41866 | 0.48018 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | unilateral_drift | TRUE | 2.875 | 1 | 3 | 3 | 4 | 3 | 1 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 1.608 | 2.1059 | 0.86111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | unilateral_step | TRUE | 2.8125 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2.25 | 2.1875 | 2.1875 | 2.1875 | 2.1875 | 0.94906 | 1.1744 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | unilateral_freeze | TRUE | 2.325 | 2 | 4 | 2 | 4 | 2 | 2 | 2 | 2.9 | 2.675 | 2.675 | 2.675 | 2.675 | 0.85619 | 1.0427 | 0.57639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | unilateral_spike | TRUE | 2.7375 | 3 | 2 | 2 | 2 | 2 | 2 | 4 | 2.35 | 2.2625 | 2.2625 | 2 | 2.525 | 0.60669 | 0.79818 | 0.31944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | distribution_location | TRUE | 3.0625 | 1 | 2 | 2 | 5 | 2 | 1 | 1 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 1.5356 | 1.9759 | 0.875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | distribution_scale | TRUE | 3.1375 | 3 | 2 | 1 | 2 | 1 | 3 | 4 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.125 | 0.55302 | 0.67633 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | distribution_tail | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2.525 | 0.72448 | 1.013 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | distribution_mixture | TRUE | 3.025 | 2 | 4 | 1 | 2 | 1 | 2 | 2 | 2.3 | 1.975 | 1.975 | 1.975 | 1.975 | 0.69436 | 0.79615 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | synchronous_switch | FALSE | 2.2875 | 4 | 3 | 2 | 2 | 2 | 4 | 4 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.7125 | 0.29668 | 0.30466 | 0.28472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | common_mode_drift | FALSE | 2.2875 | 4 | 3 | 2 | 2 | 2 | 4 | 4 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.7125 | 0.29668 | 0.30466 | 0.28472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | common_unequal | FALSE | 1.9875 | 2 | 5 | 5 | 2 | 5 | 2 | 3 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.275 | 0.63392 | 0.77876 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-05 | 2026-02-17 20:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 2.0268 | 2.7252 | 0.97917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | baseline | FALSE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.17979 | 0.18392 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | unilateral_drift | TRUE | 3.1375 | 2 | 1 | 3 | 3 | 3 | 2 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 1.8625 | 0.90384 | 1.1083 | 0.59722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | unilateral_step | TRUE | 3.2875 | 2 | 1 | 3 | 2 | 3 | 2 | 3 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.975 | 0.6846 | 0.80304 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | unilateral_freeze | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 4 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.05 | 0.52222 | 0.62037 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | unilateral_spike | TRUE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4.55 | 4.4125 | 4.4125 | 4.15 | 4.4125 | 0.2803 | 0.3468 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | distribution_location | TRUE | 2.6875 | 1 | 4 | 4 | 3 | 4 | 1 | 2 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.825 | 1.1834 | 1.477 | 0.74306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | distribution_scale | TRUE | 1.65 | 4 | 4 | 2 | 5 | 2 | 4 | 4 | 3.8 | 3.35 | 3.35 | 3.35 | 3.35 | 0.34911 | 0.40129 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | distribution_tail | TRUE | 0.85 | 4 | 4 | 4 | 5 | 4 | 3 | 5 | 4.2 | 4.15 | 4.15 | 3.6375 | 4.4125 | 0.33188 | 0.45127 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | distribution_mixture | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 3 | 3 | 3.7 | 3.275 | 3.275 | 3.275 | 3.275 | 0.53533 | 0.58203 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | synchronous_switch | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.16241 | 0.19198 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | common_mode_drift | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.16241 | 0.19198 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | common_unequal | FALSE | 2.1375 | 3 | 2 | 3 | 5 | 3 | 3 | 3 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.58679 | 0.67706 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-06 | 2026-02-22 01:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 1.2647 | 1.6032 | 0.75694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | baseline | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.20742 | 0.23922 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | unilateral_drift | TRUE | 2.4 | 2 | 2 | 3 | 5 | 3 | 2 | 2 | 2.8 | 2.6 | 2.6 | 2.6 | 2.6 | 1.0594 | 1.3166 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | unilateral_step | TRUE | 2.55 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.82491 | 0.9906 | 0.57639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | unilateral_freeze | TRUE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 3 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.59644 | 0.68389 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | unilateral_spike | TRUE | 1.0625 | 4 | 5 | 3 | 5 | 3 | 3 | 5 | 4.25 | 3.9375 | 3.9375 | 3.675 | 4.2 | 0.36303 | 0.49393 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 4 | 5 | 4 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.4596 | 1.8725 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | distribution_scale | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.43227 | 0.53063 | 0.28472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | distribution_tail | TRUE | 1.325 | 3 | 5 | 3 | 5 | 3 | 3 | 5 | 3.9 | 3.675 | 3.675 | 3.675 | 4.2 | 0.47488 | 0.64795 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | distribution_mixture | TRUE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 3 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.56629 | 0.629 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.16126 | 0.17618 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.16126 | 0.17618 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | common_unequal | FALSE | 2.2125 | 2 | 3 | 3 | 5 | 3 | 2 | 3 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.3 | 0.68804 | 0.82266 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-07 | 2026-02-26 07:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 4 | 5 | 4 | 1 | 2 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 1.653 | 2.2272 | 0.79167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | baseline | FALSE | 2.2 | 5 | 1 | 4 | 3 | 4 | 5 | 5 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 0.1412 | 0.15664 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | unilateral_drift | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 2 | 3.2 | 2.65 | 2.65 | 2.65 | 3.1625 | 1.1475 | 1.4634 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | unilateral_step | TRUE | 2.1375 | 2 | 5 | 3 | 3 | 3 | 2 | 3 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.375 | 0.74527 | 0.91804 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | unilateral_freeze | TRUE | 3.4375 | 2 | 1 | 1 | 3 | 1 | 2 | 3 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.825 | 0.76569 | 0.94745 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | unilateral_spike | TRUE | 2.2 | 5 | 1 | 4 | 3 | 4 | 4 | 5 | 3.4 | 2.8 | 2.8 | 2.5375 | 2.8 | 0.26637 | 0.35136 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | distribution_location | TRUE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 2 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 1.2347 | 1.5624 | 0.74306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | distribution_scale | TRUE | 2.7625 | 4 | 1 | 2 | 3 | 2 | 3 | 5 | 2.65 | 2.2375 | 2.2375 | 1.975 | 2.5 | 0.35857 | 0.44022 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | distribution_tail | TRUE | 2.6125 | 4 | 1 | 3 | 3 | 3 | 3 | 5 | 2.85 | 2.3875 | 2.3875 | 2.125 | 2.65 | 0.32747 | 0.45782 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | distribution_mixture | TRUE | 2.1 | 3 | 3 | 2 | 5 | 2 | 3 | 4 | 3.2 | 2.9 | 2.9 | 2.9 | 3.1625 | 0.46485 | 0.53863 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | synchronous_switch | FALSE | 2.325 | 4 | 2 | 2 | 3 | 2 | 4 | 4 | 2.9 | 2.675 | 2.675 | 2.675 | 2.675 | 0.3462 | 0.40107 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | common_mode_drift | FALSE | 2.325 | 4 | 2 | 2 | 3 | 2 | 4 | 4 | 2.9 | 2.675 | 2.675 | 2.675 | 2.675 | 0.3462 | 0.40107 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | common_unequal | FALSE | 1.7 | 3 | 3 | 4 | 4 | 4 | 3 | 4 | 3.4 | 3.3 | 3.3 | 3.3 | 3.5625 | 0.55211 | 0.67944 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-08 | 2026-03-02 12:00 | opposite_direction | FALSE | 2.7625 | 1 | 2 | 4 | 5 | 4 | 1 | 1 | 2.65 | 2.2375 | 2.2375 | 2.2375 | 2.2375 | 2.0645 | 2.8019 | 0.95833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | baseline | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.21865 | 0.23479 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | unilateral_drift | TRUE | 3.25 | 1 | 1 | 3 | 4 | 3 | 1 | 2 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 1.197 | 1.5228 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | unilateral_step | TRUE | 2.7 | 2 | 2 | 2 | 4 | 2 | 2 | 2 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 0.75775 | 0.89255 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | unilateral_freeze | TRUE | 2.325 | 2 | 4 | 2 | 4 | 2 | 2 | 3 | 2.9 | 2.675 | 2.675 | 2.675 | 2.9375 | 0.61497 | 0.72402 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | unilateral_spike | TRUE | 0.8125 | 4 | 5 | 4 | 4 | 4 | 4 | 5 | 4.25 | 4.1875 | 4.1875 | 4.1875 | 4.45 | 0.33913 | 0.43096 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | distribution_location | TRUE | 2.35 | 1 | 5 | 4 | 4 | 4 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.5076 | 1.9478 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | distribution_scale | TRUE | 1.6125 | 4 | 5 | 2 | 4 | 2 | 4 | 4 | 3.85 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 0.33886 | 0.38884 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | distribution_tail | TRUE | 1.475 | 3 | 5 | 3 | 4 | 3 | 3 | 5 | 3.7 | 3.525 | 3.525 | 3.525 | 4.05 | 0.49363 | 0.65606 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | distribution_mixture | TRUE | 2.0625 | 3 | 4 | 2 | 4 | 2 | 3 | 4 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 3.2 | 0.48442 | 0.5481 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.2254 | 0.22289 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.2254 | 0.22289 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | common_unequal | FALSE | 2.55 | 2 | 2 | 3 | 4 | 3 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.81356 | 0.99483 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-09 | 2026-03-06 17:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 2.1625 | 1.4783 | 1.9314 | 0.79861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | baseline | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.22322 | 0.26093 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | unilateral_drift | TRUE | 2.55 | 2 | 2 | 4 | 3 | 4 | 2 | 3 | 2.6 | 2.45 | 2.45 | 2.45 | 2.7125 | 0.73583 | 0.90232 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | unilateral_step | TRUE | 2.4375 | 3 | 2 | 3 | 3 | 3 | 3 | 4 | 2.75 | 2.5625 | 2.5625 | 2.5625 | 2.825 | 0.46701 | 0.52835 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | unilateral_freeze | TRUE | 2.425 | 3 | 5 | 1 | 3 | 1 | 2 | 4 | 3.1 | 2.575 | 2.575 | 2.3125 | 2.8375 | 0.61003 | 0.77135 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | unilateral_spike | TRUE | 1.2125 | 4 | 5 | 4 | 3 | 4 | 4 | 5 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 4.05 | 0.30137 | 0.39581 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 4 | 3 | 4 | 1 | 2 | 3 | 2.5 | 2.5 | 2.5 | 3.0125 | 1.1649 | 1.4832 | 0.6875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | distribution_scale | TRUE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.21748 | 0.25135 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | distribution_tail | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 4 | 5 | 4.6 | 4.2 | 4.2 | 3.9375 | 4.2 | 0.25452 | 0.35475 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 4 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.41384 | 0.44436 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | synchronous_switch | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.16674 | 0.17142 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | common_mode_drift | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.16674 | 0.17142 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | common_unequal | FALSE | 1.5875 | 4 | 3 | 4 | 3 | 4 | 3 | 5 | 3.55 | 3.4125 | 3.4125 | 3.15 | 3.675 | 0.35955 | 0.44647 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-10 | 2026-03-10 22:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 2.1625 | 1.413 | 1.818 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | baseline | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.16575 | 0.19292 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | unilateral_drift | TRUE | 2.4 | 2 | 2 | 3 | 5 | 3 | 2 | 2 | 2.8 | 2.6 | 2.6 | 2.6 | 2.6 | 0.99483 | 1.246 | 0.61806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | unilateral_step | TRUE | 2.3625 | 2 | 3 | 2 | 5 | 2 | 2 | 3 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.9 | 0.62269 | 0.74152 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | unilateral_freeze | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 2 | 4 | 3.7 | 3.275 | 3.275 | 3.0125 | 3.5375 | 0.6102 | 0.79015 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | unilateral_spike | TRUE | 0.4 | 5 | 5 | 4 | 5 | 4 | 4 | 5 | 4.8 | 4.6 | 4.6 | 4.3375 | 4.6 | 0.23944 | 0.31574 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | distribution_location | TRUE | 2.05 | 1 | 5 | 5 | 5 | 5 | 1 | 2 | 3.6 | 2.95 | 2.95 | 2.95 | 3.4625 | 1.39 | 1.775 | 0.8125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | distribution_scale | TRUE | 1.0625 | 4 | 5 | 3 | 5 | 3 | 4 | 5 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 4.2 | 0.30706 | 0.359 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | distribution_tail | TRUE | 1.175 | 3 | 5 | 4 | 5 | 4 | 3 | 5 | 4.1 | 3.825 | 3.825 | 3.825 | 4.6 | 0.43529 | 0.59585 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | distribution_mixture | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.46109 | 0.50922 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.13789 | 0.13722 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.13789 | 0.13722 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | common_unequal | FALSE | 1.3625 | 3 | 4 | 4 | 5 | 4 | 2 | 4 | 3.85 | 3.6375 | 3.6375 | 3.125 | 4.15 | 0.6003 | 0.74588 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-11 | 2026-03-15 03:00 | opposite_direction | FALSE | 2.8 | 1 | 1 | 5 | 5 | 5 | 1 | 1 | 2.6 | 2.2 | 2.2 | 2.2 | 2.2 | 1.5002 | 1.9448 | 0.83333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | baseline | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.18701 | 0.21447 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | unilateral_drift | TRUE | 2.4 | 2 | 2 | 3 | 5 | 3 | 2 | 3 | 2.8 | 2.6 | 2.6 | 2.6 | 2.8625 | 0.67957 | 0.81317 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | unilateral_step | TRUE | 2.1 | 3 | 3 | 2 | 5 | 2 | 3 | 3 | 3.2 | 2.9 | 2.9 | 2.9 | 2.9 | 0.45569 | 0.48633 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | unilateral_freeze | TRUE | 1.9875 | 2 | 5 | 2 | 5 | 2 | 2 | 3 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.275 | 0.73976 | 0.92738 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | unilateral_spike | TRUE | 0 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4.4875 | 5 | 0.27561 | 0.35288 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | distribution_location | TRUE | 1.9875 | 2 | 5 | 5 | 2 | 5 | 2 | 2 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.0125 | 1.0806 | 1.3566 | 0.66667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 3 | 5 | 3 | 4 | 5 | 4.6 | 4.2 | 4.2 | 3.9375 | 4.2 | 0.25487 | 0.29515 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | distribution_tail | TRUE | 0 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4.4875 | 5 | 0.25154 | 0.34979 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | distribution_mixture | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 4 | 4 | 3.7 | 3.275 | 3.275 | 3.5375 | 3.5375 | 0.40197 | 0.43383 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | synchronous_switch | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.14898 | 0.15571 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | common_mode_drift | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.14898 | 0.15571 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | common_unequal | FALSE | 1.4375 | 4 | 3 | 3 | 5 | 3 | 3 | 4 | 3.75 | 3.5625 | 3.5625 | 3.3 | 3.5625 | 0.38346 | 0.44002 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-12 | 2026-03-19 08:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 4 | 5 | 4 | 1 | 2 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 1.2273 | 1.5455 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | baseline | FALSE | 2.3625 | 2 | 3 | 4 | 3 | 4 | 2 | 3 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 3.15 | 0.77062 | 0.9464 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | unilateral_drift | TRUE | 3.025 | 3 | 1 | 4 | 1 | 4 | 3 | 4 | 2.3 | 1.975 | 1.975 | 1.975 | 2.2375 | 0.43304 | 0.5273 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | unilateral_step | TRUE | 2.875 | 4 | 2 | 2 | 1 | 2 | 4 | 5 | 2.5 | 2.125 | 2.125 | 2.125 | 2.3875 | 0.31751 | 0.36252 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | unilateral_freeze | TRUE | 3.1375 | 1 | 4 | 1 | 3 | 1 | 1 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.125 | 1.3216 | 1.7444 | 0.6875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | unilateral_spike | TRUE | 2.175 | 2 | 4 | 4 | 3 | 4 | 2 | 3 | 3.1 | 2.825 | 2.825 | 2.825 | 3.3375 | 0.88831 | 1.1379 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | distribution_location | TRUE | 2.3625 | 2 | 3 | 4 | 3 | 4 | 2 | 4 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 3.4125 | 0.63178 | 0.78907 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | distribution_scale | TRUE | 2.3625 | 2 | 3 | 4 | 3 | 4 | 2 | 3 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 3.15 | 0.69171 | 0.87044 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | distribution_tail | TRUE | 2.025 | 2 | 4 | 5 | 3 | 5 | 2 | 3 | 3.3 | 2.975 | 2.975 | 2.975 | 3.4875 | 0.76023 | 0.96613 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | distribution_mixture | TRUE | 2.575 | 3 | 5 | 2 | 1 | 2 | 3 | 4 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.44771 | 0.47767 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | synchronous_switch | FALSE | 2.3125 | 3 | 4 | 5 | 1 | 5 | 3 | 3 | 3.25 | 2.6875 | 2.6875 | 2.6875 | 2.6875 | 0.59041 | 0.71087 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | common_mode_drift | FALSE | 2.3125 | 3 | 4 | 5 | 1 | 5 | 3 | 3 | 3.25 | 2.6875 | 2.6875 | 2.6875 | 2.6875 | 0.59041 | 0.71087 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | common_unequal | FALSE | 2.3125 | 5 | 2 | 4 | 1 | 4 | 5 | 5 | 3.25 | 2.6875 | 2.6875 | 2.6875 | 2.6875 | 0.16318 | 0.21641 | 0.083333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-13 | 2026-03-23 14:00 | opposite_direction | FALSE | 3.2875 | 2 | 1 | 4 | 1 | 4 | 2 | 2 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.7125 | 1.0207 | 1.2706 | 0.64583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | baseline | FALSE | 1.2875 | 5 | 4 | 3 | 3 | 3 | 5 | 5 | 3.95 | 3.7125 | 3.7125 | 3.7125 | 3.7125 | 0.20421 | 0.22923 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | unilateral_drift | TRUE | 2.7 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 2.4 | 2.3 | 2.3 | 2.3 | 2.5625 | 0.6941 | 0.85591 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | unilateral_step | TRUE | 2.5875 | 3 | 2 | 2 | 3 | 2 | 3 | 4 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.675 | 0.46484 | 0.54788 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | unilateral_freeze | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 4 | 2.5 | 2.125 | 2.125 | 2.125 | 2.65 | 0.62093 | 0.79415 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | unilateral_spike | TRUE | 1.4 | 4 | 4 | 4 | 3 | 4 | 3 | 5 | 3.8 | 3.6 | 3.6 | 3.3375 | 3.8625 | 0.34145 | 0.45797 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | distribution_location | TRUE | 2.8375 | 1 | 4 | 3 | 3 | 3 | 1 | 2 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.675 | 1.2486 | 1.5996 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | distribution_scale | TRUE | 1.4 | 4 | 4 | 4 | 3 | 4 | 4 | 5 | 3.8 | 3.6 | 3.6 | 3.6 | 3.8625 | 0.30189 | 0.37815 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | distribution_tail | TRUE | 1.4 | 4 | 4 | 4 | 3 | 4 | 3 | 5 | 3.8 | 3.6 | 3.6 | 3.3375 | 3.8625 | 0.31912 | 0.46242 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 4 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.43954 | 0.48719 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.19503 | 0.19542 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.19503 | 0.19542 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | common_unequal | FALSE | 1.7375 | 4 | 3 | 3 | 3 | 3 | 3 | 4 | 3.35 | 3.2625 | 3.2625 | 3 | 3.2625 | 0.39919 | 0.47087 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-14 | 2026-03-27 19:00 | opposite_direction | FALSE | 2.9875 | 2 | 1 | 4 | 3 | 4 | 2 | 2 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 1.0882 | 1.2998 | 0.77083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | baseline | FALSE | 1.9375 | 5 | 4 | 4 | 1 | 4 | 5 | 5 | 3.75 | 3.0625 | 3.0625 | 3.0625 | 3.0625 | 0.13169 | 0.14078 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | unilateral_drift | TRUE | 2.7 | 2 | 2 | 4 | 2 | 4 | 2 | 2 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 1.0739 | 1.3547 | 0.65278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | unilateral_step | TRUE | 3.25 | 2 | 2 | 3 | 1 | 3 | 2 | 2 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 0.8012 | 0.96497 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | unilateral_freeze | TRUE | 2.8375 | 2 | 5 | 2 | 1 | 2 | 2 | 3 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.425 | 0.80536 | 1.0089 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | unilateral_spike | TRUE | 1.75 | 5 | 5 | 4 | 1 | 4 | 4 | 5 | 4 | 3.25 | 3.25 | 2.9875 | 3.25 | 0.21876 | 0.29516 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | distribution_location | TRUE | 2.8375 | 1 | 4 | 4 | 2 | 4 | 1 | 2 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.675 | 1.3732 | 1.7563 | 0.79861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | distribution_scale | TRUE | 2.35 | 4 | 4 | 3 | 1 | 3 | 4 | 5 | 3.2 | 2.65 | 2.65 | 2.65 | 2.9125 | 0.32215 | 0.37489 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | distribution_tail | TRUE | 2.275 | 3 | 5 | 4 | 1 | 4 | 3 | 5 | 3.3 | 2.725 | 2.725 | 2.725 | 3.25 | 0.42037 | 0.57562 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | distribution_mixture | TRUE | 2.575 | 3 | 5 | 2 | 1 | 2 | 3 | 4 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.46555 | 0.52129 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | synchronous_switch | FALSE | 1.5 | 5 | 5 | 3 | 2 | 3 | 5 | 5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 0.13281 | 0.14265 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | common_mode_drift | FALSE | 1.5 | 5 | 5 | 3 | 2 | 3 | 5 | 5 | 4 | 3.5 | 3.5 | 3.5 | 3.5 | 0.13281 | 0.14265 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | common_unequal | FALSE | 2.175 | 2 | 4 | 5 | 2 | 5 | 2 | 3 | 3.1 | 2.825 | 2.825 | 2.825 | 3.0875 | 0.63906 | 0.76418 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-15 | 2026-04-01 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 1.507 | 1.9747 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | baseline | FALSE | 0.8125 | 4 | 5 | 4 | 4 | 4 | 4 | 5 | 4.25 | 4.1875 | 4.1875 | 4.1875 | 4.45 | 0.32555 | 0.38054 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | unilateral_drift | TRUE | 2.55 | 2 | 2 | 3 | 4 | 3 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.72648 | 0.85895 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | unilateral_step | TRUE | 2.4375 | 3 | 2 | 2 | 4 | 2 | 3 | 4 | 2.75 | 2.5625 | 2.5625 | 2.5625 | 2.825 | 0.50867 | 0.58852 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | unilateral_freeze | TRUE | 2.25 | 3 | 3 | 2 | 4 | 2 | 3 | 4 | 3 | 2.75 | 2.75 | 2.75 | 3.0125 | 0.49096 | 0.57753 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | unilateral_spike | TRUE | 1.325 | 3 | 5 | 4 | 4 | 4 | 3 | 5 | 3.9 | 3.675 | 3.675 | 3.675 | 4.45 | 0.43409 | 0.56145 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | distribution_location | TRUE | 1.8375 | 2 | 5 | 4 | 4 | 4 | 2 | 2 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 3.1625 | 1.057 | 1.3358 | 0.63889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | distribution_scale | TRUE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.45148 | 0.55339 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | distribution_tail | TRUE | 0.8125 | 4 | 5 | 4 | 4 | 4 | 3 | 5 | 4.25 | 4.1875 | 4.1875 | 3.675 | 4.45 | 0.389 | 0.53258 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | distribution_mixture | TRUE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 3 | 3.5 | 3.125 | 3.125 | 3.125 | 3.125 | 0.53661 | 0.59805 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | synchronous_switch | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.206 | 0.2276 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | common_mode_drift | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.206 | 0.2276 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | common_unequal | FALSE | 1.85 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 3.2 | 3.15 | 3.15 | 3.15 | 3.4125 | 0.44613 | 0.51207 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-16 | 2026-04-05 05:00 | opposite_direction | FALSE | 2.8 | 1 | 1 | 5 | 5 | 5 | 1 | 2 | 2.6 | 2.2 | 2.2 | 2.2 | 2.4625 | 1.165 | 1.488 | 0.68056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | baseline | FALSE | 1.325 | 5 | 3 | 4 | 3 | 4 | 5 | 5 | 3.9 | 3.675 | 3.675 | 3.675 | 3.675 | 0.21569 | 0.24837 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | unilateral_drift | TRUE | 2.5375 | 1 | 4 | 4 | 4 | 4 | 1 | 2 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.975 | 1.218 | 1.53 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | unilateral_step | TRUE | 2.475 | 2 | 4 | 2 | 3 | 2 | 2 | 2 | 2.7 | 2.525 | 2.525 | 2.525 | 2.525 | 0.75438 | 0.90081 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | unilateral_freeze | TRUE | 2.2875 | 2 | 5 | 2 | 3 | 2 | 2 | 3 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.975 | 0.71322 | 0.88314 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | unilateral_spike | TRUE | 1.5875 | 4 | 3 | 4 | 3 | 4 | 3 | 5 | 3.55 | 3.4125 | 3.4125 | 3.15 | 3.675 | 0.34881 | 0.47024 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | distribution_location | TRUE | 2.725 | 1 | 3 | 4 | 4 | 4 | 1 | 2 | 2.7 | 2.275 | 2.275 | 2.275 | 2.7875 | 1.4477 | 1.8711 | 0.8125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | distribution_scale | TRUE | 2.5875 | 3 | 2 | 2 | 3 | 2 | 3 | 5 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.9375 | 0.41099 | 0.51832 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | distribution_tail | TRUE | 1.85 | 3 | 3 | 4 | 3 | 4 | 3 | 5 | 3.2 | 3.15 | 3.15 | 3.15 | 3.675 | 0.50547 | 0.67578 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 4 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.52423 | 0.60519 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | synchronous_switch | FALSE | 1.175 | 5 | 3 | 4 | 4 | 4 | 5 | 5 | 4.1 | 3.825 | 3.825 | 3.825 | 3.825 | 0.19036 | 0.19226 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | common_mode_drift | FALSE | 1.175 | 5 | 3 | 4 | 4 | 4 | 5 | 5 | 4.1 | 3.825 | 3.825 | 3.825 | 3.825 | 0.19036 | 0.19226 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | common_unequal | FALSE | 1.8375 | 2 | 5 | 4 | 4 | 4 | 2 | 3 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 3.675 | 0.7476 | 0.91729 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-17 | 2026-04-09 10:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.7037 | 2.2423 | 0.89583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | baseline | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.076249 | 0.080785 | 0.069444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | unilateral_drift | TRUE | 2.7 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 2.4 | 2.3 | 2.3 | 2.3 | 2.5625 | 0.75393 | 0.91858 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | unilateral_step | TRUE | 2.5875 | 3 | 2 | 2 | 3 | 2 | 3 | 3 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.4125 | 0.55711 | 0.60444 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | unilateral_freeze | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 4 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.56917 | 0.68472 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | unilateral_spike | TRUE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.17688 | 0.24388 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | distribution_location | TRUE | 2.5375 | 1 | 4 | 5 | 3 | 5 | 1 | 2 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.975 | 1.2245 | 1.5825 | 0.6875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | distribution_scale | TRUE | 1.7375 | 4 | 3 | 3 | 3 | 3 | 4 | 5 | 3.35 | 3.2625 | 3.2625 | 3.2625 | 3.525 | 0.29997 | 0.37032 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | distribution_tail | TRUE | 1.2125 | 4 | 5 | 4 | 3 | 4 | 4 | 5 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 4.05 | 0.31272 | 0.41934 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | distribution_mixture | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 4 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.05 | 0.41045 | 0.47112 | 0.31944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.10082 | 0.098585 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.10082 | 0.098585 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | common_unequal | FALSE | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3.2625 | 0.45088 | 0.52925 | 0.33333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO12 | PAIR_DO12-18 | 2026-04-13 16:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 2 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 1.2171 | 1.5192 | 0.76389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | baseline | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.21686 | 0.25958 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | unilateral_drift | TRUE | 2.3625 | 2 | 3 | 2 | 5 | 2 | 2 | 2 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.80462 | 0.9938 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | unilateral_step | TRUE | 2.1 | 3 | 3 | 2 | 5 | 2 | 2 | 3 | 3.2 | 2.9 | 2.9 | 2.6375 | 2.9 | 0.60115 | 0.72413 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | unilateral_freeze | TRUE | 2.95 | 2 | 2 | 1 | 5 | 1 | 2 | 4 | 2.4 | 2.05 | 2.05 | 2.05 | 2.575 | 0.65194 | 0.89212 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | unilateral_spike | TRUE | 0.5125 | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 4.65 | 4.4875 | 4.4875 | 4.4875 | 5 | 0.31898 | 0.42515 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | distribution_location | TRUE | 2.05 | 1 | 5 | 5 | 5 | 5 | 1 | 2 | 3.6 | 2.95 | 2.95 | 2.95 | 3.4625 | 1.3833 | 1.7869 | 0.77778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | distribution_scale | TRUE | 0.8 | 5 | 5 | 3 | 5 | 3 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.23169 | 0.26115 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | distribution_tail | TRUE | 1.025 | 3 | 5 | 5 | 5 | 5 | 3 | 5 | 4.3 | 3.975 | 3.975 | 3.975 | 5 | 0.46071 | 0.64285 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | distribution_mixture | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.4353 | 0.46161 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.1281 | 0.13943 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.1281 | 0.13943 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | common_unequal | FALSE | 1.5125 | 3 | 4 | 3 | 5 | 3 | 3 | 4 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 3.75 | 0.49871 | 0.62286 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-01 | 2026-02-01 | opposite_direction | FALSE | 3.25 | 1 | 1 | 2 | 5 | 2 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.4295 | 1.8177 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | baseline | FALSE | 2.725 | 4 | 2 | 3 | 1 | 3 | 4 | 5 | 2.7 | 2.275 | 2.275 | 2.275 | 2.5375 | 0.3016 | 0.35452 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | unilateral_drift | TRUE | 2.6875 | 2 | 5 | 3 | 1 | 3 | 2 | 2 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 0.90851 | 1.1114 | 0.60417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | unilateral_step | TRUE | 2.8375 | 2 | 5 | 2 | 1 | 2 | 2 | 3 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.425 | 0.63625 | 0.72708 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | unilateral_freeze | TRUE | 3.7375 | 2 | 1 | 1 | 1 | 1 | 2 | 4 | 1.35 | 1.2625 | 1.2625 | 1.2625 | 1.7875 | 0.65895 | 0.88066 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | unilateral_spike | TRUE | 2.725 | 4 | 2 | 3 | 1 | 3 | 3 | 5 | 2.7 | 2.275 | 2.275 | 2.0125 | 2.5375 | 0.37213 | 0.49059 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | distribution_location | TRUE | 3.3625 | 1 | 2 | 3 | 2 | 3 | 1 | 1 | 1.85 | 1.6375 | 1.6375 | 1.6375 | 1.6375 | 1.6357 | 2.1059 | 0.93056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | distribution_scale | TRUE | 2.1625 | 5 | 2 | 5 | 1 | 5 | 5 | 5 | 3.45 | 2.8375 | 2.8375 | 2.8375 | 2.8375 | 0.13241 | 0.1466 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | distribution_tail | TRUE | 2.9875 | 3 | 2 | 3 | 1 | 3 | 3 | 5 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.5375 | 0.49936 | 0.68411 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | distribution_mixture | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 3 | 3 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 0.48066 | 0.4724 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | synchronous_switch | FALSE | 2.0875 | 5 | 4 | 3 | 1 | 3 | 5 | 5 | 3.55 | 2.9125 | 2.9125 | 2.9125 | 2.9125 | 0.23724 | 0.23799 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | common_mode_drift | FALSE | 2.0875 | 5 | 4 | 3 | 1 | 3 | 5 | 5 | 3.55 | 2.9125 | 2.9125 | 2.9125 | 2.9125 | 0.23724 | 0.23799 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | common_unequal | FALSE | 2.125 | 3 | 5 | 5 | 1 | 5 | 3 | 4 | 3.5 | 2.875 | 2.875 | 2.875 | 3.1375 | 0.51389 | 0.58334 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-02 | 2026-02-05 05:00 | opposite_direction | FALSE | 3.5125 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 1.4875 | 1.8325 | 2.3968 | 0.98611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | baseline | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.1085 | 0.11139 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | unilateral_drift | TRUE | 2.55 | 2 | 2 | 4 | 3 | 4 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.87989 | 1.0683 | 0.59722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | unilateral_step | TRUE | 2.5875 | 3 | 2 | 2 | 3 | 2 | 3 | 3 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.4125 | 0.57134 | 0.65593 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | unilateral_freeze | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 4 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.05 | 0.47915 | 0.59025 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | unilateral_spike | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.18716 | 0.23323 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | distribution_location | TRUE | 2.3875 | 1 | 4 | 5 | 4 | 5 | 1 | 2 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 3.125 | 1.2331 | 1.5598 | 0.74306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | distribution_scale | TRUE | 1.2875 | 5 | 4 | 3 | 3 | 3 | 4 | 5 | 3.95 | 3.7125 | 3.7125 | 3.45 | 3.7125 | 0.28214 | 0.32672 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | distribution_tail | TRUE | 1.4 | 4 | 4 | 4 | 3 | 4 | 3 | 5 | 3.8 | 3.6 | 3.6 | 3.3375 | 3.8625 | 0.33732 | 0.44182 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 4 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.40928 | 0.46453 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.11738 | 0.11694 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.11738 | 0.11694 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | common_unequal | FALSE | 1.85 | 3 | 3 | 4 | 3 | 4 | 3 | 3 | 3.2 | 3.15 | 3.15 | 3.15 | 3.15 | 0.57726 | 0.67506 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-03 | 2026-02-09 10:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.4883 | 1.9342 | 0.81944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | baseline | FALSE | 2.025 | 4 | 2 | 4 | 3 | 4 | 3 | 5 | 3.3 | 2.975 | 2.975 | 2.7125 | 3.2375 | 0.36538 | 0.47471 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | unilateral_drift | TRUE | 1.8375 | 2 | 5 | 5 | 3 | 5 | 2 | 2 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 3.1625 | 0.73929 | 0.87104 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | unilateral_step | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 3 | 4 | 3.85 | 3.6375 | 3.6375 | 3.375 | 3.6375 | 0.39429 | 0.47659 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | unilateral_freeze | TRUE | 3.4375 | 2 | 1 | 1 | 3 | 1 | 2 | 4 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 2.0875 | 0.7891 | 1.1253 | 0.28472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | unilateral_spike | TRUE | 2.2875 | 3 | 2 | 4 | 3 | 4 | 3 | 5 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 3.2375 | 0.4091 | 0.56146 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | distribution_location | TRUE | 2.55 | 2 | 2 | 4 | 3 | 4 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 1.0891 | 1.3614 | 0.68056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | distribution_scale | TRUE | 2.025 | 4 | 2 | 4 | 3 | 4 | 4 | 5 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.32571 | 0.39933 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | distribution_tail | TRUE | 1.7625 | 5 | 2 | 4 | 3 | 4 | 4 | 5 | 3.65 | 3.2375 | 3.2375 | 2.975 | 3.2375 | 0.25799 | 0.36053 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | distribution_mixture | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 3 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 2.7875 | 0.43768 | 0.45168 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | synchronous_switch | FALSE | 1.7375 | 4 | 3 | 3 | 3 | 3 | 4 | 4 | 3.35 | 3.2625 | 3.2625 | 3.2625 | 3.2625 | 0.35369 | 0.40431 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | common_mode_drift | FALSE | 1.7375 | 4 | 3 | 3 | 3 | 3 | 4 | 4 | 3.35 | 3.2625 | 3.2625 | 3.2625 | 3.2625 | 0.35369 | 0.40431 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | common_unequal | FALSE | 1.6625 | 3 | 4 | 4 | 3 | 4 | 3 | 4 | 3.45 | 3.3375 | 3.3375 | 3.3375 | 3.6 | 0.41472 | 0.47823 | 0.31944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-04 | 2026-02-13 15:00 | opposite_direction | FALSE | 2.9125 | 1 | 2 | 5 | 3 | 5 | 1 | 1 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.0875 | 1.5272 | 1.9898 | 0.83333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | baseline | FALSE | 1.7 | 3 | 3 | 3 | 5 | 3 | 3 | 4 | 3.4 | 3.3 | 3.3 | 3.3 | 3.5625 | 0.50955 | 0.58999 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | unilateral_drift | TRUE | 2.0625 | 2 | 3 | 4 | 5 | 4 | 2 | 3 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 3.45 | 0.68395 | 0.86213 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | unilateral_step | TRUE | 0.85 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 4.2 | 4.15 | 4.15 | 4.15 | 4.15 | 0.37498 | 0.42589 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | unilateral_freeze | TRUE | 2.7625 | 2 | 3 | 1 | 5 | 1 | 2 | 4 | 2.65 | 2.2375 | 2.2375 | 2.2375 | 2.7625 | 0.71818 | 0.93308 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | unilateral_spike | TRUE | 2.0625 | 2 | 3 | 4 | 5 | 4 | 2 | 4 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 3.7125 | 0.61323 | 0.76743 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | distribution_location | TRUE | 2.2125 | 2 | 3 | 3 | 5 | 3 | 2 | 2 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 2.7875 | 0.96823 | 1.2063 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | distribution_scale | TRUE | 1.9875 | 3 | 2 | 4 | 5 | 4 | 3 | 4 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.275 | 0.42365 | 0.5209 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | distribution_tail | TRUE | 1.55 | 3 | 3 | 4 | 5 | 4 | 3 | 4 | 3.6 | 3.45 | 3.45 | 3.45 | 3.7125 | 0.51767 | 0.66834 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | distribution_mixture | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 3 | 3 | 3.7 | 3.275 | 3.275 | 3.275 | 3.275 | 0.44219 | 0.45457 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | synchronous_switch | FALSE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 3 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.5074 | 0.52623 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | common_mode_drift | FALSE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 3 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.5074 | 0.52623 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | common_unequal | FALSE | 0.8 | 5 | 5 | 3 | 5 | 3 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.24847 | 0.26597 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-05 | 2026-02-17 20:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.5445 | 1.9631 | 0.91667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | baseline | FALSE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.18213 | 0.18318 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | unilateral_drift | TRUE | 2.25 | 2 | 2 | 4 | 5 | 4 | 2 | 2 | 3 | 2.75 | 2.75 | 2.75 | 2.75 | 0.88769 | 1.1137 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | unilateral_step | TRUE | 2.1375 | 3 | 2 | 3 | 5 | 3 | 3 | 3 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.58673 | 0.69548 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | unilateral_freeze | TRUE | 2.3125 | 3 | 4 | 1 | 5 | 1 | 2 | 4 | 3.25 | 2.6875 | 2.6875 | 2.425 | 2.95 | 0.56392 | 0.71765 | 0.33333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | unilateral_spike | TRUE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4.55 | 4.4125 | 4.4125 | 4.15 | 4.4125 | 0.26074 | 0.32346 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | distribution_location | TRUE | 2.3875 | 1 | 4 | 4 | 5 | 4 | 1 | 2 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 3.125 | 1.319 | 1.703 | 0.74306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | distribution_scale | TRUE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.19161 | 0.23602 | 0.125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | distribution_tail | TRUE | 0.7 | 4 | 4 | 5 | 5 | 5 | 3 | 5 | 4.4 | 4.3 | 4.3 | 3.7875 | 4.5625 | 0.3664 | 0.46715 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | distribution_mixture | TRUE | 1.65 | 4 | 4 | 2 | 5 | 2 | 4 | 4 | 3.8 | 3.35 | 3.35 | 3.35 | 3.35 | 0.39488 | 0.41739 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.09841 | 0.10383 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.09841 | 0.10383 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | common_unequal | FALSE | 1.9875 | 3 | 2 | 4 | 5 | 4 | 3 | 4 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.275 | 0.55355 | 0.65407 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-06 | 2026-02-22 01:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 4 | 5 | 4 | 1 | 2 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 1.2612 | 1.6159 | 0.72917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | baseline | FALSE | 1.6125 | 5 | 2 | 4 | 4 | 4 | 5 | 5 | 3.85 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 0.17476 | 0.18941 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | unilateral_drift | TRUE | 1.8375 | 2 | 5 | 4 | 4 | 4 | 2 | 2 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 3.1625 | 0.976 | 1.2146 | 0.61806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | unilateral_step | TRUE | 1.8125 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3.25 | 3.1875 | 3.1875 | 3.1875 | 3.1875 | 0.57181 | 0.66135 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | unilateral_freeze | TRUE | 2.8375 | 3 | 2 | 1 | 4 | 1 | 3 | 4 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.425 | 0.47164 | 0.56848 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | unilateral_spike | TRUE | 1.4625 | 5 | 2 | 5 | 4 | 5 | 4 | 5 | 4.05 | 3.5375 | 3.5375 | 3.275 | 3.5375 | 0.26387 | 0.34257 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | distribution_location | TRUE | 2.7625 | 1 | 2 | 4 | 5 | 4 | 1 | 2 | 2.65 | 2.2375 | 2.2375 | 2.2375 | 2.75 | 1.1401 | 1.4279 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | distribution_scale | TRUE | 1.7625 | 5 | 2 | 3 | 4 | 3 | 4 | 5 | 3.65 | 3.2375 | 3.2375 | 2.975 | 3.2375 | 0.24889 | 0.28518 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | distribution_tail | TRUE | 1.9 | 5 | 1 | 5 | 4 | 5 | 4 | 5 | 3.8 | 3.1 | 3.1 | 2.8375 | 3.1 | 0.22009 | 0.29737 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | distribution_mixture | TRUE | 2.0625 | 3 | 4 | 2 | 4 | 2 | 3 | 4 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 3.2 | 0.4316 | 0.46933 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | synchronous_switch | FALSE | 2.1375 | 4 | 3 | 2 | 3 | 2 | 4 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.31783 | 0.33065 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | common_mode_drift | FALSE | 2.1375 | 4 | 3 | 2 | 3 | 2 | 4 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.31783 | 0.33065 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | common_unequal | FALSE | 1.8125 | 3 | 4 | 3 | 3 | 3 | 3 | 4 | 3.25 | 3.1875 | 3.1875 | 3.1875 | 3.45 | 0.51272 | 0.58138 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-07 | 2026-02-26 07:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 2.1625 | 1.9714 | 2.7486 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | baseline | FALSE | 1.6125 | 5 | 2 | 4 | 4 | 4 | 5 | 5 | 3.85 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 0.24219 | 0.28328 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | unilateral_drift | TRUE | 1.9875 | 2 | 5 | 3 | 4 | 3 | 2 | 2 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.0125 | 1.0927 | 1.3952 | 0.63889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | unilateral_step | TRUE | 1.8375 | 2 | 5 | 4 | 4 | 4 | 2 | 3 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 3.675 | 0.63581 | 0.75875 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | unilateral_freeze | TRUE | 2.725 | 2 | 4 | 1 | 4 | 1 | 2 | 4 | 2.7 | 2.275 | 2.275 | 2.275 | 2.8 | 0.62263 | 0.77845 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | unilateral_spike | TRUE | 1.875 | 4 | 2 | 4 | 4 | 4 | 4 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.292 | 0.3663 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | distribution_location | TRUE | 2.9125 | 1 | 2 | 4 | 4 | 4 | 1 | 2 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.6 | 1.1861 | 1.5139 | 0.69444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | distribution_scale | TRUE | 2.025 | 4 | 2 | 3 | 4 | 3 | 4 | 5 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.28601 | 0.33316 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | distribution_tail | TRUE | 1.175 | 5 | 3 | 4 | 4 | 4 | 4 | 5 | 4.1 | 3.825 | 3.825 | 3.5625 | 3.825 | 0.26608 | 0.3555 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | distribution_mixture | TRUE | 1.8 | 4 | 4 | 2 | 4 | 2 | 4 | 4 | 3.6 | 3.2 | 3.2 | 3.2 | 3.2 | 0.3814 | 0.43196 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | synchronous_switch | FALSE | 2.4375 | 3 | 2 | 2 | 4 | 2 | 3 | 4 | 2.75 | 2.5625 | 2.5625 | 2.5625 | 2.825 | 0.50469 | 0.63282 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | common_mode_drift | FALSE | 2.4375 | 3 | 2 | 2 | 4 | 2 | 3 | 4 | 2.75 | 2.5625 | 2.5625 | 2.5625 | 2.825 | 0.50469 | 0.63282 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | common_unequal | FALSE | 2.175 | 2 | 4 | 3 | 4 | 3 | 2 | 4 | 3.1 | 2.825 | 2.825 | 2.825 | 3.6 | 0.64271 | 0.81193 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-08 | 2026-03-02 12:00 | opposite_direction | FALSE | 3.2125 | 1 | 2 | 2 | 4 | 2 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 1.5947 | 2.0189 | 0.95833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | baseline | FALSE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 4 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.05 | 0.4095 | 0.47879 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | unilateral_drift | TRUE | 2.7 | 2 | 2 | 3 | 3 | 3 | 2 | 2 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 0.73439 | 0.87213 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | unilateral_step | TRUE | 2.5875 | 3 | 2 | 2 | 3 | 2 | 3 | 3 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.4125 | 0.51442 | 0.53328 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | unilateral_freeze | TRUE | 2.6875 | 2 | 5 | 1 | 3 | 1 | 2 | 3 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.575 | 0.79185 | 1.0049 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | unilateral_spike | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 4 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.05 | 0.51046 | 0.64706 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | distribution_location | TRUE | 2.9875 | 1 | 4 | 2 | 3 | 2 | 1 | 1 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 1.5187 | 1.9478 | 0.875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | distribution_scale | TRUE | 1.325 | 5 | 3 | 4 | 3 | 4 | 5 | 5 | 3.9 | 3.675 | 3.675 | 3.675 | 3.675 | 0.17824 | 0.18596 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | distribution_tail | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 2 | 5 | 3.05 | 2.7875 | 2.7875 | 2.525 | 3.3125 | 0.55485 | 0.76734 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 3 | 3.3 | 2.975 | 2.975 | 2.975 | 2.975 | 0.47445 | 0.4713 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | synchronous_switch | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.10427 | 0.10897 | 0.097222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | common_mode_drift | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.10427 | 0.10897 | 0.097222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | common_unequal | FALSE | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3.2625 | 0.41686 | 0.46792 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-09 | 2026-03-06 17:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 2.1625 | 1.1811 | 1.4593 | 0.76389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | baseline | FALSE | 1.1 | 5 | 5 | 3 | 3 | 3 | 5 | 5 | 4.2 | 3.9 | 3.9 | 3.9 | 3.9 | 0.22956 | 0.27611 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | unilateral_drift | TRUE | 2.55 | 2 | 2 | 4 | 3 | 4 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 1.1049 | 1.3878 | 0.68056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | unilateral_step | TRUE | 2.7 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 2.4 | 2.3 | 2.3 | 2.3 | 2.5625 | 0.65923 | 0.80243 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | unilateral_freeze | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 4 | 2.5 | 2.125 | 2.125 | 2.125 | 2.65 | 0.73856 | 0.95779 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | unilateral_spike | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 4 | 5 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 3.9 | 0.31475 | 0.432 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | distribution_location | TRUE | 2.65 | 1 | 5 | 3 | 3 | 3 | 1 | 2 | 2.8 | 2.35 | 2.35 | 2.35 | 2.8625 | 1.4599 | 1.8914 | 0.8125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | distribution_scale | TRUE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.089505 | 0.098249 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | distribution_tail | TRUE | 1.475 | 3 | 5 | 4 | 3 | 4 | 3 | 5 | 3.7 | 3.525 | 3.525 | 3.525 | 4.05 | 0.40902 | 0.57059 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 4 | 3.3 | 2.975 | 2.975 | 2.975 | 3.2375 | 0.42566 | 0.45944 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | synchronous_switch | FALSE | 1.1 | 5 | 5 | 3 | 3 | 3 | 5 | 5 | 4.2 | 3.9 | 3.9 | 3.9 | 3.9 | 0.15624 | 0.16318 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | common_mode_drift | FALSE | 1.1 | 5 | 5 | 3 | 3 | 3 | 5 | 5 | 4.2 | 3.9 | 3.9 | 3.9 | 3.9 | 0.15624 | 0.16318 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | common_unequal | FALSE | 2.3625 | 2 | 3 | 4 | 3 | 4 | 2 | 3 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 3.15 | 0.67924 | 0.83114 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-10 | 2026-03-10 22:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 3 | 3 | 3 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.609 | 2.0705 | 0.91667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | baseline | FALSE | 2.7375 | 3 | 2 | 2 | 2 | 2 | 3 | 4 | 2.35 | 2.2625 | 2.2625 | 2.2625 | 2.525 | 0.47765 | 0.54609 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | unilateral_drift | TRUE | 3.1375 | 2 | 1 | 4 | 2 | 4 | 2 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 1.8625 | 0.93751 | 1.1366 | 0.63889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | unilateral_step | TRUE | 3.2875 | 2 | 1 | 3 | 2 | 3 | 2 | 3 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.975 | 0.62495 | 0.73602 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | unilateral_freeze | TRUE | 3.5875 | 2 | 1 | 1 | 2 | 1 | 2 | 3 | 1.55 | 1.4125 | 1.4125 | 1.4125 | 1.675 | 0.7624 | 0.98363 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | unilateral_spike | TRUE | 2.7375 | 3 | 2 | 2 | 2 | 2 | 3 | 4 | 2.35 | 2.2625 | 2.2625 | 2.2625 | 2.525 | 0.54286 | 0.67791 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | distribution_location | TRUE | 3.5125 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 1.4875 | 1.6509 | 2.1913 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | distribution_scale | TRUE | 1.725 | 5 | 3 | 4 | 2 | 4 | 5 | 5 | 3.7 | 3.275 | 3.275 | 3.275 | 3.275 | 0.25214 | 0.27208 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | distribution_tail | TRUE | 2.5875 | 3 | 2 | 3 | 2 | 3 | 2 | 4 | 2.55 | 2.4125 | 2.4125 | 2.15 | 2.675 | 0.6078 | 0.76299 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | distribution_mixture | TRUE | 2.3625 | 3 | 4 | 2 | 2 | 2 | 3 | 3 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.47032 | 0.45516 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | synchronous_switch | FALSE | 1.875 | 5 | 3 | 3 | 2 | 3 | 5 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.125 | 0.19986 | 0.18495 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | common_mode_drift | FALSE | 1.875 | 5 | 3 | 3 | 2 | 3 | 5 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.125 | 0.19986 | 0.18495 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | common_unequal | FALSE | 3.2875 | 2 | 1 | 3 | 2 | 3 | 2 | 3 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.975 | 0.68125 | 0.81134 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-11 | 2026-03-15 03:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 3 | 2 | 3 | 1 | 2 | 1.6 | 1.45 | 1.45 | 1.45 | 1.7125 | 1.1614 | 1.4449 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | baseline | FALSE | 1.7375 | 4 | 3 | 3 | 3 | 3 | 4 | 5 | 3.35 | 3.2625 | 3.2625 | 3.2625 | 3.525 | 0.31069 | 0.3604 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | unilateral_drift | TRUE | 3.1375 | 2 | 1 | 3 | 3 | 3 | 2 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 1.8625 | 0.83111 | 1.0241 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | unilateral_step | TRUE | 2.5875 | 3 | 2 | 2 | 3 | 2 | 3 | 3 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.4125 | 0.58399 | 0.66314 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | unilateral_freeze | TRUE | 3.25 | 2 | 2 | 1 | 3 | 1 | 2 | 4 | 2 | 1.75 | 1.75 | 1.75 | 2.275 | 0.61873 | 0.80899 | 0.33333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | unilateral_spike | TRUE | 2.175 | 4 | 2 | 3 | 3 | 3 | 3 | 5 | 3.1 | 2.825 | 2.825 | 2.5625 | 3.0875 | 0.36507 | 0.45567 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | distribution_location | TRUE | 3.025 | 1 | 3 | 3 | 3 | 3 | 1 | 2 | 2.3 | 1.975 | 1.975 | 1.975 | 2.4875 | 1.5011 | 1.9787 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | distribution_scale | TRUE | 1.175 | 5 | 3 | 5 | 3 | 5 | 5 | 5 | 4.1 | 3.825 | 3.825 | 3.825 | 3.825 | 0.13771 | 0.1323 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | distribution_tail | TRUE | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 3.2625 | 0.46194 | 0.59398 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | distribution_mixture | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 3 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 2.7875 | 0.44904 | 0.45211 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | synchronous_switch | FALSE | 1.2875 | 5 | 4 | 3 | 3 | 3 | 5 | 5 | 3.95 | 3.7125 | 3.7125 | 3.7125 | 3.7125 | 0.19257 | 0.19595 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | common_mode_drift | FALSE | 1.2875 | 5 | 4 | 3 | 3 | 3 | 5 | 5 | 3.95 | 3.7125 | 3.7125 | 3.7125 | 3.7125 | 0.19257 | 0.19595 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | common_unequal | FALSE | 2.4375 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 2.75 | 2.5625 | 2.5625 | 2.5625 | 2.5625 | 0.58432 | 0.6822 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-12 | 2026-03-19 08:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 2 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 1.1468 | 1.4114 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | baseline | FALSE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1.0673 | 1.2973 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | unilateral_drift | TRUE | 2.4625 | 4 | 1 | 5 | 2 | 5 | 4 | 4 | 3.05 | 2.5375 | 2.5375 | 2.5375 | 2.5375 | 0.35116 | 0.40009 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | unilateral_step | TRUE | 2.475 | 4 | 2 | 2 | 2 | 2 | 4 | 4 | 2.7 | 2.525 | 2.525 | 2.525 | 2.525 | 0.31725 | 0.31115 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | unilateral_freeze | TRUE | 3.85 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 1.2 | 1.15 | 1.15 | 1.15 | 1.4125 | 1.3576 | 1.7534 | 0.76389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | unilateral_spike | TRUE | 3.5125 | 1 | 2 | 2 | 2 | 2 | 1 | 2 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 2 | 1.1864 | 1.5098 | 0.70139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | distribution_location | TRUE | 2.85 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2.2 | 2.15 | 2.15 | 2.15 | 2.15 | 0.79026 | 0.96524 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | distribution_scale | TRUE | 2.85 | 2 | 2 | 3 | 2 | 3 | 2 | 2 | 2.2 | 2.15 | 2.15 | 2.15 | 2.15 | 0.95638 | 1.1866 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | distribution_tail | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1.025 | 1.2963 | 0.61806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 2 | 3.1 | 2.825 | 2.825 | 2.825 | 2.5625 | 0.54493 | 0.54711 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | synchronous_switch | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.6 | 0.77475 | 0.97644 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | common_mode_drift | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.6 | 0.77475 | 0.97644 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | common_unequal | FALSE | 2.35 | 5 | 1 | 4 | 2 | 4 | 5 | 5 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 0.1892 | 0.2181 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-13 | 2026-03-23 14:00 | opposite_direction | FALSE | 3.5875 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 1.55 | 1.4125 | 1.4125 | 1.4125 | 1.4125 | 0.79223 | 0.96853 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | baseline | FALSE | 2.2875 | 4 | 3 | 2 | 2 | 2 | 4 | 5 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.975 | 0.32019 | 0.37625 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | unilateral_drift | TRUE | 3.1375 | 2 | 1 | 4 | 2 | 4 | 2 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 1.8625 | 0.8996 | 1.0827 | 0.625 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | unilateral_step | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 2.2625 | 2.2625 | 0.61306 | 0.68843 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | unilateral_freeze | TRUE | 3.4 | 2 | 2 | 1 | 2 | 1 | 2 | 4 | 1.8 | 1.6 | 1.6 | 1.6 | 2.125 | 0.62646 | 0.8404 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | unilateral_spike | TRUE | 2.55 | 3 | 3 | 2 | 2 | 2 | 3 | 5 | 2.6 | 2.45 | 2.45 | 2.45 | 2.975 | 0.40563 | 0.5279 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | distribution_location | TRUE | 3.325 | 1 | 3 | 2 | 2 | 2 | 1 | 1 | 1.9 | 1.675 | 1.675 | 1.675 | 1.675 | 1.6771 | 2.1794 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | distribution_scale | TRUE | 1.725 | 5 | 3 | 4 | 2 | 4 | 5 | 5 | 3.7 | 3.275 | 3.275 | 3.275 | 3.275 | 0.09195 | 0.088435 | 0.097222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | distribution_tail | TRUE | 2.55 | 3 | 3 | 2 | 2 | 2 | 2 | 5 | 2.6 | 2.45 | 2.45 | 2.1875 | 2.975 | 0.52993 | 0.74896 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 3 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.48171 | 0.50192 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | synchronous_switch | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.12927 | 0.1136 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | common_mode_drift | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.12927 | 0.1136 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | common_unequal | FALSE | 2.85 | 2 | 2 | 3 | 2 | 3 | 2 | 3 | 2.2 | 2.15 | 2.15 | 2.15 | 2.4125 | 0.62286 | 0.71402 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-14 | 2026-03-27 19:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 3 | 2 | 3 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.2209 | 1.4701 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | baseline | FALSE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 4 | 3.1 | 2.825 | 2.825 | 2.825 | 3.0875 | 0.45643 | 0.56165 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | unilateral_drift | TRUE | 3.25 | 2 | 2 | 3 | 1 | 3 | 2 | 3 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 0.70999 | 0.86851 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | unilateral_step | TRUE | 2.95 | 3 | 3 | 2 | 1 | 2 | 3 | 3 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 0.50804 | 0.53655 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | unilateral_freeze | TRUE | 2.8375 | 2 | 5 | 1 | 2 | 1 | 2 | 3 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.425 | 0.86579 | 1.1421 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | unilateral_spike | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 4 | 3.1 | 2.825 | 2.825 | 2.825 | 3.0875 | 0.49207 | 0.6303 | 0.28472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | distribution_location | TRUE | 2.95 | 1 | 5 | 2 | 2 | 2 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.5011 | 1.9416 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | distribution_scale | TRUE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.2379 | 0.27613 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | distribution_tail | TRUE | 2.025 | 3 | 5 | 3 | 2 | 3 | 2 | 5 | 3.3 | 2.975 | 2.975 | 2.7125 | 3.5 | 0.51298 | 0.72071 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 3 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.45439 | 0.46102 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.16729 | 0.1816 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.16729 | 0.1816 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | common_unequal | FALSE | 2.8 | 3 | 3 | 3 | 1 | 3 | 3 | 4 | 2.6 | 2.2 | 2.2 | 2.2 | 2.4625 | 0.43009 | 0.47144 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-15 | 2026-04-01 | opposite_direction | FALSE | 3.4 | 1 | 1 | 5 | 1 | 5 | 1 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 1.2132 | 1.5127 | 0.76389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | baseline | FALSE | 1.2125 | 4 | 5 | 3 | 4 | 3 | 4 | 4 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.7875 | 0.36977 | 0.42648 | 0.28472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | unilateral_drift | TRUE | 2.9125 | 1 | 2 | 4 | 4 | 4 | 1 | 2 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.6 | 1.2901 | 1.6224 | 0.79167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | unilateral_step | TRUE | 2.3625 | 2 | 3 | 3 | 4 | 3 | 2 | 3 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 3.15 | 0.7639 | 0.94447 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | unilateral_freeze | TRUE | 2.9125 | 2 | 3 | 1 | 4 | 1 | 2 | 3 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.35 | 0.84389 | 1.0778 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | unilateral_spike | TRUE | 1.475 | 3 | 5 | 3 | 4 | 3 | 3 | 4 | 3.7 | 3.525 | 3.525 | 3.525 | 3.7875 | 0.42369 | 0.53485 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 3 | 4 | 3 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.7516 | 2.3176 | 0.90278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | distribution_scale | TRUE | 0.7375 | 5 | 4 | 4 | 4 | 4 | 5 | 5 | 4.35 | 4.2625 | 4.2625 | 4.2625 | 4.2625 | 0.20617 | 0.22324 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | distribution_tail | TRUE | 1.475 | 3 | 5 | 3 | 4 | 3 | 2 | 4 | 3.7 | 3.525 | 3.525 | 3.0125 | 3.7875 | 0.60441 | 0.79901 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | distribution_mixture | TRUE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 2 | 3.5 | 3.125 | 3.125 | 3.125 | 2.8625 | 0.50926 | 0.49692 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | synchronous_switch | FALSE | 1.2125 | 4 | 5 | 3 | 4 | 3 | 4 | 4 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.7875 | 0.34993 | 0.40266 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | common_mode_drift | FALSE | 1.2125 | 4 | 5 | 3 | 4 | 3 | 4 | 4 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.7875 | 0.34993 | 0.40266 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | common_unequal | FALSE | 2.0625 | 2 | 3 | 5 | 4 | 5 | 2 | 2 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 2.9375 | 0.92741 | 1.1336 | 0.61806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-16 | 2026-04-05 05:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 2 | 4 | 2 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6684 | 2.1371 | 0.96528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | baseline | FALSE | 1.9125 | 5 | 2 | 4 | 2 | 4 | 5 | 5 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.25073 | 0.27899 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | unilateral_drift | TRUE | 2.175 | 2 | 4 | 5 | 2 | 5 | 2 | 2 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.94185 | 1.167 | 0.60417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | unilateral_step | TRUE | 2.2125 | 3 | 4 | 3 | 2 | 3 | 3 | 3 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 2.7875 | 0.56361 | 0.65694 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | unilateral_freeze | TRUE | 3.2125 | 2 | 3 | 1 | 2 | 1 | 2 | 4 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 2.3125 | 0.63858 | 0.84671 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | unilateral_spike | TRUE | 1.9875 | 4 | 3 | 4 | 2 | 4 | 4 | 5 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.275 | 0.34317 | 0.42844 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | distribution_location | TRUE | 2.9125 | 1 | 2 | 4 | 4 | 4 | 1 | 2 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.6 | 1.2706 | 1.6039 | 0.77083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | distribution_scale | TRUE | 1.9125 | 5 | 2 | 4 | 2 | 4 | 5 | 5 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.19867 | 0.22 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | distribution_tail | TRUE | 1.9875 | 4 | 3 | 4 | 2 | 4 | 3 | 5 | 3.35 | 3.0125 | 3.0125 | 2.75 | 3.275 | 0.34685 | 0.48549 | 0.13889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 4 | 3.1 | 2.825 | 2.825 | 2.825 | 3.0875 | 0.4384 | 0.4853 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | synchronous_switch | FALSE | 2.1375 | 4 | 3 | 3 | 2 | 3 | 4 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.30954 | 0.3446 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | common_mode_drift | FALSE | 2.1375 | 4 | 3 | 3 | 2 | 3 | 4 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.30954 | 0.3446 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | common_unequal | FALSE | 1.875 | 3 | 5 | 4 | 2 | 4 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.4885 | 0.60121 | 0.31944 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-17 | 2026-04-09 10:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.7809 | 2.3849 | 0.875 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | baseline | FALSE | 2.175 | 4 | 2 | 3 | 3 | 3 | 4 | 5 | 3.1 | 2.825 | 2.825 | 2.825 | 3.0875 | 0.3273 | 0.38346 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | unilateral_drift | TRUE | 3.1375 | 2 | 1 | 3 | 3 | 3 | 2 | 3 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.125 | 0.69465 | 0.82904 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | unilateral_step | TRUE | 2.5875 | 3 | 2 | 2 | 3 | 2 | 3 | 3 | 2.55 | 2.4125 | 2.4125 | 2.4125 | 2.4125 | 0.5088 | 0.54244 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | unilateral_freeze | TRUE | 3.4375 | 2 | 1 | 1 | 3 | 1 | 2 | 4 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 2.0875 | 0.68208 | 0.87292 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | unilateral_spike | TRUE | 2.175 | 4 | 2 | 3 | 3 | 3 | 3 | 5 | 3.1 | 2.825 | 2.825 | 2.5625 | 3.0875 | 0.38656 | 0.50074 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | distribution_location | TRUE | 3.2125 | 1 | 2 | 3 | 3 | 3 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 1.4661 | 1.8833 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | distribution_scale | TRUE | 1.7625 | 5 | 2 | 4 | 3 | 4 | 5 | 5 | 3.65 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 0.12777 | 0.13888 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | distribution_tail | TRUE | 2.4375 | 3 | 2 | 3 | 3 | 3 | 3 | 5 | 2.75 | 2.5625 | 2.5625 | 2.5625 | 3.0875 | 0.42203 | 0.60152 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | distribution_mixture | TRUE | 2.4 | 3 | 3 | 2 | 3 | 2 | 3 | 3 | 2.8 | 2.6 | 2.6 | 2.6 | 2.6 | 0.47646 | 0.48854 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | synchronous_switch | FALSE | 1.875 | 5 | 3 | 2 | 3 | 2 | 5 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.125 | 0.24174 | 0.2455 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | common_mode_drift | FALSE | 1.875 | 5 | 3 | 2 | 3 | 2 | 5 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.125 | 0.24174 | 0.2455 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | common_unequal | FALSE | 3.025 | 3 | 1 | 2 | 3 | 2 | 3 | 4 | 2.3 | 1.975 | 1.975 | 1.975 | 2.2375 | 0.48398 | 0.53349 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO13 | PAIR_DO13-18 | 2026-04-13 16:00 | opposite_direction | FALSE | 2.9875 | 2 | 1 | 4 | 3 | 4 | 2 | 2 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 1.0436 | 1.2393 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | baseline | FALSE | 1.725 | 3 | 5 | 5 | 2 | 5 | 4 | 4 | 3.7 | 3.275 | 3.275 | 3.5375 | 3.5375 | 0.40442 | 0.41477 | 0.38889 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | unilateral_drift | TRUE | 3.5125 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 1.4875 | 1.266 | 1.5591 | 0.82639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | unilateral_step | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2.2625 | 0.81693 | 1.0282 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | unilateral_freeze | TRUE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 5 | 3 | 4.05 | 3.5375 | 3.5375 | 3.8 | 3.275 | 0.36314 | 0.27652 | 0.49306 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | unilateral_spike | TRUE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.46463 | 0.5429 | 0.34722 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.5489 | 1.9148 | 1 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | distribution_scale | TRUE | 1.9125 | 3 | 4 | 5 | 2 | 5 | 3 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.35 | 0.45441 | 0.54902 | 0.3125 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | distribution_tail | TRUE | 1.9875 | 2 | 5 | 5 | 2 | 5 | 2 | 3 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.275 | 0.66553 | 0.83144 | 0.41667 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 3 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.59362 | 0.68844 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.22936 | 0.26189 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.22936 | 0.26189 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | common_unequal | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.6 | 0.77553 | 0.9546 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-01 | 2026-02-01 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.5875 | 2.0162 | 0.94444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | baseline | FALSE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 3 | 3.9 | 3.675 | 3.675 | 3.675 | 3.675 | 0.50611 | 0.53796 | 0.45833 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | unilateral_drift | TRUE | 3.2125 | 1 | 2 | 3 | 3 | 3 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 1.2729 | 1.5289 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | unilateral_step | TRUE | 2.85 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2.2 | 2.15 | 2.15 | 2.15 | 2.15 | 0.94156 | 1.1665 | 0.60417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | unilateral_freeze | TRUE | 1.8375 | 2 | 5 | 5 | 3 | 5 | 3 | 2 | 3.55 | 3.1625 | 3.1625 | 3.675 | 3.1625 | 0.62149 | 0.63766 | 0.59722 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | unilateral_spike | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 3 | 3.9 | 3.675 | 3.675 | 3.675 | 3.675 | 0.48737 | 0.52524 | 0.43056 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | distribution_location | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.486 | 1.847 | 0.94444 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | distribution_scale | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 4 | 3.9 | 3.675 | 3.675 | 3.675 | 3.9375 | 0.41954 | 0.49553 | 0.30556 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | distribution_tail | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 3 | 3.9 | 3.675 | 3.675 | 3.675 | 3.675 | 0.58571 | 0.65674 | 0.47917 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 3 | 3.3 | 2.975 | 2.975 | 2.975 | 2.975 | 0.56052 | 0.61012 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | synchronous_switch | FALSE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 4 | 4 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 3.6375 | 0.31555 | 0.28981 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | common_mode_drift | FALSE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 4 | 4 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 3.6375 | 0.31555 | 0.28981 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | common_unequal | FALSE | 2.025 | 2 | 4 | 5 | 3 | 5 | 2 | 2 | 3.3 | 2.975 | 2.975 | 2.975 | 2.975 | 0.84665 | 1.05 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-02 | 2026-02-05 05:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.59 | 2.025 | 0.9375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | baseline | FALSE | 1.65 | 4 | 4 | 5 | 2 | 5 | 4 | 5 | 3.8 | 3.35 | 3.35 | 3.35 | 3.6125 | 0.30175 | 0.33624 | 0.25 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | unilateral_drift | TRUE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 2 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.3375 | 1.0536 | 1.3254 | 0.64583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | unilateral_step | TRUE | 2.8125 | 2 | 3 | 2 | 2 | 2 | 2 | 3 | 2.25 | 2.1875 | 2.1875 | 2.1875 | 2.45 | 0.6514 | 0.76158 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | unilateral_freeze | TRUE | 1.65 | 4 | 4 | 5 | 2 | 5 | 4 | 4 | 3.8 | 3.35 | 3.35 | 3.35 | 3.35 | 0.35975 | 0.39588 | 0.30556 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | unilateral_spike | TRUE | 1.65 | 4 | 4 | 5 | 2 | 5 | 4 | 5 | 3.8 | 3.35 | 3.35 | 3.35 | 3.6125 | 0.34761 | 0.42657 | 0.22917 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | distribution_location | TRUE | 2.3875 | 1 | 4 | 5 | 4 | 5 | 1 | 1 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 1.3341 | 1.5754 | 0.97222 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | distribution_scale | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.19822 | 0.23314 | 0.14583 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | distribution_tail | TRUE | 1.2125 | 3 | 4 | 5 | 5 | 5 | 3 | 4 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 4.3 | 0.44584 | 0.57177 | 0.25694 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | distribution_mixture | TRUE | 2.175 | 3 | 5 | 2 | 2 | 2 | 3 | 3 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.52877 | 0.55721 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | synchronous_switch | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.2344 | 0.25178 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | common_mode_drift | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.2344 | 0.25178 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | common_unequal | FALSE | 2.325 | 2 | 4 | 4 | 2 | 4 | 2 | 4 | 2.9 | 2.675 | 2.675 | 2.675 | 3.2 | 0.61238 | 0.75211 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-03 | 2026-02-09 10:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.5805 | 1.9814 | 0.97917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | baseline | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.22775 | 0.18514 | 0.29167 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | unilateral_drift | TRUE | 3.6625 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 1.45 | 1.3375 | 1.3375 | 1.6 | 1.6 | 1.1572 | 1.3962 | 0.79861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | unilateral_step | TRUE | 3.2125 | 2 | 3 | 2 | 1 | 2 | 2 | 3 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 2.05 | 0.72361 | 0.87268 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | unilateral_freeze | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.28235 | 0.21132 | 0.38889 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | unilateral_spike | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 4 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 0.34261 | 0.38119 | 0.28472 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.3849 | 1.6462 | 0.99306 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.19409 | 0.14756 | 0.26389 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | distribution_tail | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 4 | 3.9 | 3.675 | 3.675 | 3.675 | 3.9375 | 0.45995 | 0.56288 | 0.30556 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | distribution_mixture | TRUE | 2.2875 | 2 | 5 | 2 | 3 | 2 | 2 | 2 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.7125 | 0.66887 | 0.74442 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.15675 | 0.1455 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.15675 | 0.1455 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | common_unequal | FALSE | 3.0625 | 2 | 3 | 3 | 1 | 3 | 2 | 2 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 0.72964 | 0.86884 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-04 | 2026-02-13 15:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 4 | 1 | 4 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.6481 | 2.1126 | 0.95139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | baseline | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 4 | 4.2 | 3.4 | 3.4 | 3.4 | 3.1375 | 0.22615 | 0.16395 | 0.31944 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | unilateral_drift | TRUE | 2.1 | 2 | 2 | 5 | 5 | 5 | 2 | 2 | 3.2 | 2.9 | 2.9 | 2.9 | 2.9 | 1.0009 | 1.1913 | 0.71528 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | unilateral_step | TRUE | 2.55 | 2 | 2 | 2 | 5 | 2 | 2 | 3 | 2.6 | 2.45 | 2.45 | 2.45 | 2.7125 | 0.68864 | 0.81903 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | unilateral_freeze | TRUE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 4 | 4.2 | 3.4 | 3.4 | 3.4 | 3.1375 | 0.28297 | 0.23551 | 0.35417 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | unilateral_spike | TRUE | 1.8625 | 4 | 5 | 5 | 1 | 5 | 4 | 4 | 3.85 | 3.1375 | 3.1375 | 3.1375 | 3.1375 | 0.32701 | 0.33668 | 0.3125 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.2537 | 1.4413 | 0.97222 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | distribution_scale | TRUE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.14274 | 0.094388 | 0.21528 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | distribution_tail | TRUE | 1.8625 | 4 | 5 | 5 | 1 | 5 | 4 | 5 | 3.85 | 3.1375 | 3.1375 | 3.1375 | 3.4 | 0.34168 | 0.42594 | 0.21528 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | distribution_mixture | TRUE | 2.8375 | 2 | 5 | 2 | 1 | 2 | 2 | 2 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 0.70137 | 0.75228 | 0.625 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.12196 | 0.12456 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.12196 | 0.12456 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | common_unequal | FALSE | 1.9125 | 2 | 3 | 5 | 5 | 5 | 3 | 3 | 3.45 | 3.0875 | 3.0875 | 3.6 | 3.6 | 0.62036 | 0.69134 | 0.51389 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-05 | 2026-02-17 20:00 | opposite_direction | FALSE | 2.8 | 1 | 1 | 5 | 5 | 5 | 1 | 1 | 2.6 | 2.2 | 2.2 | 2.2 | 2.2 | 1.8481 | 2.4413 | 0.95833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | baseline | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 4 | 4.4 | 3.8 | 3.8 | 3.8 | 3.5375 | 0.23389 | 0.15371 | 0.35417 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | unilateral_drift | TRUE | 2.4 | 2 | 2 | 3 | 5 | 3 | 2 | 1 | 2.8 | 2.6 | 2.6 | 2.6 | 2.0875 | 1.1325 | 1.3226 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | unilateral_step | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0.80186 | 0.94754 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | unilateral_freeze | TRUE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 5 | 2 | 4.05 | 3.5375 | 3.5375 | 3.8 | 3.0125 | 0.35538 | 0.20341 | 0.58333 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | unilateral_spike | TRUE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 4 | 4 | 4.05 | 3.5375 | 3.5375 | 3.5375 | 3.5375 | 0.33379 | 0.33873 | 0.32639 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.3436 | 1.5726 | 1 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | distribution_scale | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 4 | 4.4 | 3.8 | 3.8 | 3.8 | 3.5375 | 0.17843 | 0.10756 | 0.28472 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | distribution_tail | TRUE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.44815 | 0.50618 | 0.36111 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | distribution_mixture | TRUE | 2.4375 | 2 | 5 | 2 | 2 | 2 | 2 | 2 | 2.75 | 2.5625 | 2.5625 | 2.5625 | 2.5625 | 0.69065 | 0.78997 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.12931 | 0.14144 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.12931 | 0.14144 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | common_unequal | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 2 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.3375 | 0.72412 | 0.82261 | 0.57639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-06 | 2026-02-22 01:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 4 | 5 | 4 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.6201 | 2.0336 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | baseline | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 4 | 4.4 | 3.8 | 3.8 | 3.8 | 3.5375 | 0.23208 | 0.13217 | 0.38194 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | unilateral_drift | TRUE | 3.4 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.0661 | 1.2352 | 0.8125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | unilateral_step | TRUE | 3.4 | 2 | 2 | 2 | 1 | 2 | 2 | 3 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 0.71161 | 0.85268 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | unilateral_freeze | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 4 | 4.4 | 3.8 | 3.8 | 3.8 | 3.5375 | 0.24006 | 0.14085 | 0.38889 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | unilateral_spike | TRUE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 4 | 4 | 4.05 | 3.5375 | 3.5375 | 3.5375 | 3.5375 | 0.34534 | 0.33482 | 0.36111 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.2911 | 1.4852 | 1 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | distribution_scale | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 4 | 4.4 | 3.8 | 3.8 | 3.8 | 3.5375 | 0.20523 | 0.11056 | 0.34722 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | distribution_tail | TRUE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.41416 | 0.47267 | 0.32639 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | distribution_mixture | TRUE | 2.4375 | 2 | 5 | 2 | 2 | 2 | 2 | 2 | 2.75 | 2.5625 | 2.5625 | 2.5625 | 2.5625 | 0.71023 | 0.81798 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | synchronous_switch | FALSE | 1.75 | 5 | 5 | 4 | 1 | 4 | 5 | 5 | 4 | 3.25 | 3.25 | 3.25 | 3.25 | 0.074629 | 0.064196 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | common_mode_drift | FALSE | 1.75 | 5 | 5 | 4 | 1 | 4 | 5 | 5 | 4 | 3.25 | 3.25 | 3.25 | 3.25 | 0.074629 | 0.064196 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | common_unequal | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 2 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.3375 | 0.66059 | 0.73525 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-07 | 2026-02-26 07:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.4953 | 1.8347 | 0.98611 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | baseline | FALSE | 1.725 | 3 | 5 | 5 | 2 | 5 | 4 | 2 | 3.7 | 3.275 | 3.275 | 3.5375 | 3.0125 | 0.40924 | 0.31169 | 0.55556 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | unilateral_drift | TRUE | 2.85 | 2 | 2 | 3 | 2 | 3 | 2 | 1 | 2.2 | 2.15 | 2.15 | 2.15 | 1.6375 | 1.1326 | 1.3228 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | unilateral_step | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0.92225 | 1.051 | 0.72917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | unilateral_freeze | TRUE | 1.175 | 3 | 5 | 5 | 4 | 5 | 4 | 2 | 4.1 | 3.825 | 3.825 | 4.3375 | 3.3125 | 0.50563 | 0.3566 | 0.72917 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | unilateral_spike | TRUE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 5 | 2 | 4.05 | 3.5375 | 3.5375 | 3.8 | 3.0125 | 0.36103 | 0.2406 | 0.54167 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.3534 | 1.6215 | 0.95139 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | distribution_scale | TRUE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 4 | 3 | 4.05 | 3.5375 | 3.5375 | 3.5375 | 3.275 | 0.34083 | 0.28564 | 0.42361 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | distribution_tail | TRUE | 1.175 | 3 | 5 | 5 | 4 | 5 | 4 | 2 | 4.1 | 3.825 | 3.825 | 4.3375 | 3.3125 | 0.44859 | 0.37728 | 0.55556 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | distribution_mixture | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 2 | 2 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.73216 | 0.85916 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 4 | 5 | 4.2 | 3.4 | 3.4 | 3.1375 | 3.4 | 0.2085 | 0.28732 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 4 | 5 | 4.2 | 3.4 | 3.4 | 3.1375 | 3.4 | 0.2085 | 0.28732 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | common_unequal | FALSE | 3.0625 | 2 | 3 | 3 | 1 | 3 | 2 | 2 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 0.79447 | 0.89819 | 0.63889 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-08 | 2026-03-02 12:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.559 | 1.9827 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | baseline | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.19759 | 0.12098 | 0.3125 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | unilateral_drift | TRUE | 3.4 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.3375 | 1.1002 | 1.255 | 0.86806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | unilateral_step | TRUE | 3.4 | 2 | 2 | 2 | 1 | 2 | 2 | 3 | 1.8 | 1.6 | 1.6 | 1.6 | 1.8625 | 0.75256 | 0.92093 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | unilateral_freeze | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.2305 | 0.1388 | 0.36806 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | unilateral_spike | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 4 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 0.29755 | 0.29222 | 0.30556 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.303 | 1.505 | 1 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.15506 | 0.096398 | 0.24306 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | distribution_tail | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 4 | 3.9 | 3.675 | 3.675 | 3.675 | 3.9375 | 0.40522 | 0.45777 | 0.32639 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | distribution_mixture | TRUE | 2.2875 | 2 | 5 | 2 | 3 | 2 | 2 | 3 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.975 | 0.70963 | 0.84013 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.070283 | 0.066212 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.070283 | 0.066212 | 0.076389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | common_unequal | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 3 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.6 | 0.65856 | 0.75502 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-09 | 2026-03-06 17:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 5 | 1 | 5 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.5552 | 1.9253 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | baseline | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 3 | 4.6 | 4.2 | 4.2 | 4.2 | 3.675 | 0.25581 | 0.11617 | 0.46528 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | unilateral_drift | TRUE | 2.85 | 2 | 2 | 2 | 3 | 2 | 2 | 1 | 2.2 | 2.15 | 2.15 | 2.15 | 1.6375 | 1.1263 | 1.3123 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | unilateral_step | TRUE | 2.85 | 2 | 2 | 2 | 3 | 2 | 2 | 3 | 2.2 | 2.15 | 2.15 | 2.15 | 2.4125 | 0.76869 | 0.94782 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | unilateral_freeze | TRUE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 5 | 3.975 | 0.28199 | 0.13664 | 0.5 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | unilateral_spike | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 3 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.675 | 0.36978 | 0.31538 | 0.45139 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.3374 | 1.5623 | 1 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.20999 | 0.095362 | 0.38194 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | distribution_tail | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 3 | 3.9 | 3.675 | 3.675 | 3.675 | 3.675 | 0.47624 | 0.48355 | 0.46528 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | distribution_mixture | TRUE | 2.2875 | 2 | 5 | 2 | 3 | 2 | 2 | 2 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.7125 | 0.7577 | 0.85543 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.077587 | 0.069126 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.077587 | 0.069126 | 0.090278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | common_unequal | FALSE | 2.5125 | 2 | 3 | 3 | 3 | 3 | 2 | 2 | 2.65 | 2.4875 | 2.4875 | 2.4875 | 2.4875 | 0.71239 | 0.81231 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-10 | 2026-03-10 22:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.5822 | 1.975 | 0.99306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | baseline | FALSE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 3 | 2 | 3.95 | 3.4625 | 3.4625 | 3.975 | 3.4625 | 0.72724 | 0.71207 | 0.75 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | unilateral_drift | TRUE | 3.0625 | 1 | 2 | 3 | 4 | 3 | 1 | 1 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 1.3232 | 1.6543 | 0.82639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | unilateral_step | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1.0302 | 1.2031 | 0.77083 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | unilateral_freeze | TRUE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 3 | 2 | 3.95 | 3.4625 | 3.4625 | 3.975 | 3.4625 | 0.6401 | 0.55294 | 0.77083 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | unilateral_spike | TRUE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 2 | 2 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.80167 | 0.85464 | 0.72222 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | distribution_location | TRUE | 2.05 | 1 | 5 | 5 | 5 | 5 | 1 | 1 | 3.6 | 2.95 | 2.95 | 2.95 | 2.95 | 1.7245 | 2.2121 | 0.99306 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | distribution_scale | TRUE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 2 | 2 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.84621 | 0.96591 | 0.66667 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | distribution_tail | TRUE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 2 | 2 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.97724 | 1.1287 | 0.75 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | distribution_mixture | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 2 | 2 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.64485 | 0.71827 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | synchronous_switch | FALSE | 1.875 | 3 | 5 | 4 | 2 | 4 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.41033 | 0.44777 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | common_mode_drift | FALSE | 1.875 | 3 | 5 | 4 | 2 | 4 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.41033 | 0.44777 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | common_unequal | FALSE | 2.175 | 2 | 4 | 3 | 4 | 3 | 2 | 2 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.89776 | 1.112 | 0.57639 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-11 | 2026-03-15 03:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.7818 | 2.3446 | 0.9375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | baseline | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.10391 | 0.10837 | 0.097222 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | unilateral_drift | TRUE | 2.7 | 2 | 2 | 3 | 3 | 3 | 2 | 2 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 0.92773 | 1.1157 | 0.64583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | unilateral_step | TRUE | 2.85 | 2 | 2 | 2 | 3 | 2 | 3 | 3 | 2.2 | 2.15 | 2.15 | 2.4125 | 2.4125 | 0.62465 | 0.70312 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | unilateral_freeze | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 3 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.675 | 0.37747 | 0.29115 | 0.50694 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | unilateral_spike | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 4 | 5 | 4.6 | 4.2 | 4.2 | 3.9375 | 4.2 | 0.21504 | 0.29359 | 0.097222 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | distribution_location | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.3009 | 1.5431 | 0.9375 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | distribution_scale | TRUE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.2049 | 0.2628 | 0.11806 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | distribution_tail | TRUE | 1.25 | 4 | 4 | 5 | 3 | 5 | 3 | 5 | 4 | 3.75 | 3.75 | 3.4875 | 4.0125 | 0.33702 | 0.45986 | 0.15278 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 3 | 3.3 | 2.975 | 2.975 | 2.975 | 2.975 | 0.56252 | 0.61808 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.11691 | 0.10689 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.11691 | 0.10689 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | common_unequal | FALSE | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0.5668 | 0.653 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-12 | 2026-03-19 08:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 2.1625 | 1.2508 | 1.5476 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | baseline | FALSE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 4 | 3 | 4.05 | 3.5375 | 3.5375 | 3.5375 | 3.275 | 0.39731 | 0.36125 | 0.45139 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | unilateral_drift | TRUE | 2.85 | 2 | 2 | 3 | 2 | 3 | 2 | 2 | 2.2 | 2.15 | 2.15 | 2.15 | 2.15 | 0.97939 | 1.1971 | 0.65278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | unilateral_step | TRUE | 2.3625 | 3 | 4 | 2 | 2 | 2 | 3 | 3 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.60785 | 0.67976 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | unilateral_freeze | TRUE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 2 | 3.7 | 3.275 | 3.275 | 3.275 | 3.0125 | 0.5143 | 0.47754 | 0.56944 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | unilateral_spike | TRUE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 3 | 3.7 | 3.275 | 3.275 | 3.275 | 3.275 | 0.46618 | 0.50382 | 0.40972 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.2266 | 1.4471 | 0.89583 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | distribution_scale | TRUE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.45398 | 0.56219 | 0.29167 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | distribution_tail | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 4 | 3.9 | 3.675 | 3.675 | 3.675 | 3.9375 | 0.51448 | 0.61673 | 0.36111 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | distribution_mixture | TRUE | 2.6625 | 2 | 3 | 2 | 3 | 2 | 3 | 3 | 2.45 | 2.3375 | 2.3375 | 2.6 | 2.6 | 0.61779 | 0.6917 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | synchronous_switch | FALSE | 1.75 | 5 | 5 | 4 | 1 | 4 | 5 | 5 | 4 | 3.25 | 3.25 | 3.25 | 3.25 | 0.25781 | 0.28154 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | common_mode_drift | FALSE | 1.75 | 5 | 5 | 4 | 1 | 4 | 5 | 5 | 4 | 3.25 | 3.25 | 3.25 | 3.25 | 0.25781 | 0.28154 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | common_unequal | FALSE | 2.0625 | 3 | 4 | 4 | 2 | 4 | 3 | 4 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 3.2 | 0.52213 | 0.62485 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-13 | 2026-03-23 14:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.4549 | 1.8508 | 0.86111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | baseline | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.18391 | 0.13985 | 0.25 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | unilateral_drift | TRUE | 2.55 | 2 | 2 | 3 | 4 | 3 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 1.0463 | 1.2763 | 0.70139 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | unilateral_step | TRUE | 2.7 | 2 | 2 | 2 | 4 | 2 | 2 | 3 | 2.4 | 2.3 | 2.3 | 2.3 | 2.5625 | 0.69679 | 0.83261 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | unilateral_freeze | TRUE | 0.6625 | 4 | 5 | 5 | 4 | 5 | 5 | 4 | 4.45 | 4.3375 | 4.3375 | 4.6 | 4.3375 | 0.30583 | 0.26898 | 0.36111 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | unilateral_spike | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 4 | 5 | 4.8 | 4.6 | 4.6 | 4.3375 | 4.6 | 0.2657 | 0.29469 | 0.22222 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.3102 | 1.5263 | 0.98611 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | distribution_scale | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.13092 | 0.11171 | 0.15972 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | distribution_tail | TRUE | 0.6625 | 4 | 5 | 5 | 4 | 5 | 3 | 5 | 4.45 | 4.3375 | 4.3375 | 3.825 | 4.6 | 0.34768 | 0.48224 | 0.14583 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | distribution_mixture | TRUE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 3 | 3.5 | 3.125 | 3.125 | 3.125 | 3.125 | 0.60438 | 0.6647 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | synchronous_switch | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.20837 | 0.18524 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | common_mode_drift | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 4.6 | 4.45 | 4.45 | 4.45 | 4.45 | 0.20837 | 0.18524 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | common_unequal | FALSE | 2.2125 | 2 | 3 | 4 | 4 | 4 | 2 | 2 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 2.7875 | 0.70143 | 0.77553 | 0.59028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-14 | 2026-03-27 19:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.7462 | 2.2854 | 0.9375 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | baseline | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.12913 | 0.085586 | 0.19444 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | unilateral_drift | TRUE | 2.7 | 2 | 2 | 3 | 3 | 3 | 2 | 1 | 2.4 | 2.3 | 2.3 | 2.3 | 1.7875 | 1.1064 | 1.2654 | 0.86806 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | unilateral_step | TRUE | 2.85 | 2 | 2 | 2 | 3 | 2 | 2 | 3 | 2.2 | 2.15 | 2.15 | 2.15 | 2.4125 | 0.73741 | 0.89568 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | unilateral_freeze | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 4 | 4.8 | 4.6 | 4.6 | 4.6 | 4.3375 | 0.25075 | 0.15866 | 0.38889 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | unilateral_spike | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.24367 | 0.28112 | 0.1875 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | distribution_location | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.3064 | 1.5154 | 0.99306 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | distribution_scale | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.054827 | 0.045081 | 0.069444 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | distribution_tail | TRUE | 0.6625 | 4 | 5 | 5 | 4 | 5 | 3 | 5 | 4.45 | 4.3375 | 4.3375 | 3.825 | 4.6 | 0.34242 | 0.45034 | 0.18056 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | distribution_mixture | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 2 | 2 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 2.8625 | 0.67664 | 0.77125 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.13298 | 0.12442 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.13298 | 0.12442 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | common_unequal | FALSE | 2.5125 | 2 | 3 | 3 | 3 | 3 | 2 | 2 | 2.65 | 2.4875 | 2.4875 | 2.4875 | 2.4875 | 0.6981 | 0.76536 | 0.59722 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-15 | 2026-04-01 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.6374 | 2.0855 | 0.96528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | baseline | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 4 | 4.8 | 4.6 | 4.6 | 4.6 | 4.3375 | 0.24945 | 0.16113 | 0.38194 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | unilateral_drift | TRUE | 2.7 | 2 | 2 | 2 | 4 | 2 | 2 | 2 | 2.4 | 2.3 | 2.3 | 2.3 | 2.3 | 1.0439 | 1.2168 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | unilateral_step | TRUE | 2.5125 | 2 | 3 | 2 | 4 | 2 | 2 | 3 | 2.65 | 2.4875 | 2.4875 | 2.4875 | 2.75 | 0.7052 | 0.84662 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | unilateral_freeze | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 4 | 4.8 | 4.6 | 4.6 | 4.6 | 4.3375 | 0.26099 | 0.1711 | 0.39583 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | unilateral_spike | TRUE | 0.6625 | 4 | 5 | 5 | 4 | 5 | 4 | 4 | 4.45 | 4.3375 | 4.3375 | 4.3375 | 4.3375 | 0.33591 | 0.32836 | 0.34722 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.2776 | 1.472 | 0.98611 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | distribution_scale | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 4 | 4.8 | 4.6 | 4.6 | 4.6 | 4.3375 | 0.21651 | 0.14326 | 0.32639 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | distribution_tail | TRUE | 1.175 | 3 | 5 | 5 | 4 | 5 | 3 | 4 | 4.1 | 3.825 | 3.825 | 3.825 | 4.3375 | 0.42085 | 0.46994 | 0.34722 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | distribution_mixture | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 2 | 3 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.125 | 0.68138 | 0.79767 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.13736 | 0.12709 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.13736 | 0.12709 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | common_unequal | FALSE | 1.5125 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 3.4875 | 0.58481 | 0.66913 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-16 | 2026-04-05 05:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.7829 | 2.3094 | 0.99306 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | baseline | FALSE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 5 | 2 | 4.25 | 3.9375 | 3.9375 | 4.2 | 3.1625 | 0.35064 | 0.19088 | 0.59028 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | unilateral_drift | TRUE | 2.85 | 2 | 2 | 3 | 2 | 3 | 2 | 2 | 2.2 | 2.15 | 2.15 | 2.15 | 2.15 | 1.1087 | 1.3062 | 0.8125 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | unilateral_step | TRUE | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0.77025 | 0.89023 | 0.59028 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | unilateral_freeze | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 5 | 2 | 4.25 | 3.9375 | 3.9375 | 4.2 | 3.1625 | 0.35378 | 0.19611 | 0.59028 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | unilateral_spike | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 4 | 2 | 3.9 | 3.675 | 3.675 | 3.9375 | 3.1625 | 0.45324 | 0.38965 | 0.54861 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.3337 | 1.5562 | 1 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | distribution_scale | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 5 | 2 | 4.25 | 3.9375 | 3.9375 | 4.2 | 3.1625 | 0.3232 | 0.17755 | 0.54167 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | distribution_tail | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 2 | 3.9 | 3.675 | 3.675 | 3.675 | 3.1625 | 0.55329 | 0.52863 | 0.59028 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | distribution_mixture | TRUE | 2.2875 | 2 | 5 | 2 | 3 | 2 | 2 | 3 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.975 | 0.67292 | 0.77893 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.11313 | 0.11448 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.11313 | 0.11448 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | common_unequal | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 2 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.3375 | 0.70597 | 0.80624 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-17 | 2026-04-09 10:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.6504 | 2.0841 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | baseline | FALSE | 1.9125 | 3 | 4 | 5 | 2 | 5 | 4 | 2 | 3.45 | 3.0875 | 3.0875 | 3.35 | 2.825 | 0.50066 | 0.42702 | 0.61111 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | unilateral_drift | TRUE | 3.2875 | 2 | 1 | 4 | 1 | 4 | 2 | 2 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.7125 | 1.1032 | 1.3757 | 0.69444 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | unilateral_step | TRUE | 3.25 | 2 | 2 | 3 | 1 | 3 | 2 | 2 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 0.74556 | 0.83518 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | unilateral_freeze | TRUE | 1.9125 | 3 | 4 | 5 | 2 | 5 | 4 | 2 | 3.45 | 3.0875 | 3.0875 | 3.35 | 2.825 | 0.50729 | 0.43807 | 0.61111 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | unilateral_spike | TRUE | 1.9125 | 3 | 4 | 5 | 2 | 5 | 3 | 2 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 2.825 | 0.58348 | 0.57895 | 0.59028 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | distribution_location | TRUE | 2.6875 | 1 | 4 | 5 | 2 | 5 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 1.3926 | 1.6543 | 1 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | distribution_scale | TRUE | 1.9125 | 3 | 4 | 5 | 2 | 5 | 4 | 2 | 3.45 | 3.0875 | 3.0875 | 3.35 | 2.825 | 0.47955 | 0.40572 | 0.59028 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | distribution_tail | TRUE | 2.175 | 2 | 4 | 5 | 2 | 5 | 3 | 2 | 3.1 | 2.825 | 2.825 | 3.0875 | 2.825 | 0.65716 | 0.68786 | 0.61111 | 1 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | distribution_mixture | TRUE | 2.575 | 3 | 5 | 2 | 1 | 2 | 3 | 3 | 2.9 | 2.425 | 2.425 | 2.425 | 2.425 | 0.54964 | 0.57347 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | synchronous_switch | FALSE | 1.6875 | 5 | 4 | 3 | 2 | 3 | 5 | 5 | 3.75 | 3.3125 | 3.3125 | 3.3125 | 3.3125 | 0.23275 | 0.2444 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | common_mode_drift | FALSE | 1.6875 | 5 | 4 | 3 | 2 | 3 | 5 | 5 | 3.75 | 3.3125 | 3.3125 | 3.3125 | 3.3125 | 0.23275 | 0.2444 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | common_unequal | FALSE | 2.85 | 2 | 2 | 3 | 2 | 3 | 2 | 2 | 2.2 | 2.15 | 2.15 | 2.15 | 2.15 | 0.7676 | 0.90434 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_DO14 | PAIR_DO14-18 | 2026-04-13 16:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.3154 | 1.5951 | 0.89583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | baseline | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.3395 | 0.34361 | 0.33333 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | unilateral_drift | TRUE | 2.175 | 2 | 4 | 4 | 3 | 4 | 2 | 1 | 3.1 | 2.825 | 2.825 | 2.825 | 2.3125 | 0.93306 | 1.0968 | 0.6875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | unilateral_step | TRUE | 2.5125 | 2 | 3 | 4 | 2 | 4 | 3 | 2 | 2.65 | 2.4875 | 2.4875 | 2.75 | 2.4875 | 0.74613 | 0.87319 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | unilateral_freeze | TRUE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 4 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.35 | 0.30198 | 0.23015 | 0.40972 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | unilateral_spike | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 4 | 5 | 4.4 | 3.8 | 3.8 | 3.5375 | 3.8 | 0.44198 | 0.52367 | 0.31944 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | distribution_location | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.4449 | 1.8386 | 0.85417 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | distribution_scale | TRUE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 5 | 4 | 4.05 | 3.5375 | 3.5375 | 3.8 | 3.5375 | 0.45816 | 0.51824 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | distribution_tail | TRUE | 1.725 | 3 | 5 | 5 | 2 | 5 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.61921 | 0.75887 | 0.40972 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | distribution_mixture | TRUE | 1.7625 | 4 | 5 | 3 | 2 | 3 | 4 | 4 | 3.65 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 0.51372 | 0.56454 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.17252 | 0.16253 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.17252 | 0.16253 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | common_unequal | FALSE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 3 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.675 | 0.56826 | 0.63228 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-01 | 2026-02-01 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.4365 | 1.8016 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | baseline | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.34941 | 0.39254 | 0.28472 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | unilateral_drift | TRUE | 2.9125 | 1 | 2 | 5 | 3 | 5 | 1 | 1 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.0875 | 1.2855 | 1.6425 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | unilateral_step | TRUE | 2.3625 | 2 | 3 | 4 | 3 | 4 | 2 | 2 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.79018 | 0.94196 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | unilateral_freeze | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.38915 | 0.37081 | 0.41667 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | unilateral_spike | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.34587 | 0.40515 | 0.25694 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.4827 | 1.8925 | 0.86806 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.27967 | 0.30408 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | distribution_tail | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 3 | 5 | 3.9 | 3.675 | 3.675 | 3.675 | 4.2 | 0.6133 | 0.8092 | 0.31944 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | distribution_mixture | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 4 | 3 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 3.375 | 0.53021 | 0.55034 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.26601 | 0.31373 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.26601 | 0.31373 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | common_unequal | FALSE | 2.0625 | 2 | 3 | 5 | 4 | 5 | 2 | 2 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 2.9375 | 0.87991 | 1.0961 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-02 | 2026-02-05 05:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.5157 | 1.9614 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | baseline | FALSE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 5 | 3 | 4.25 | 3.9375 | 3.9375 | 4.2 | 3.675 | 0.5117 | 0.51024 | 0.51389 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | unilateral_drift | TRUE | 1.85 | 3 | 3 | 4 | 3 | 4 | 3 | 2 | 3.2 | 3.15 | 3.15 | 3.15 | 2.6375 | 0.69246 | 0.79761 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | unilateral_step | TRUE | 1.5875 | 4 | 3 | 4 | 3 | 4 | 4 | 4 | 3.55 | 3.4125 | 3.4125 | 3.4125 | 3.4125 | 0.45949 | 0.52045 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | unilateral_freeze | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 5 | 2 | 4.25 | 3.9375 | 3.9375 | 4.2 | 3.1625 | 0.55469 | 0.49856 | 0.63889 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | unilateral_spike | TRUE | 1.325 | 3 | 5 | 5 | 3 | 5 | 4 | 3 | 3.9 | 3.675 | 3.675 | 3.9375 | 3.675 | 0.61187 | 0.68183 | 0.50694 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | distribution_location | TRUE | 1.8375 | 2 | 5 | 5 | 3 | 5 | 2 | 1 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 2.65 | 0.92024 | 1.0476 | 0.72917 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | distribution_scale | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 4 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 0.48515 | 0.52155 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | distribution_tail | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 3 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.675 | 0.53658 | 0.598 | 0.44444 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | distribution_mixture | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 4 | 3 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 3.375 | 0.57226 | 0.63432 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.34484 | 0.34788 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.34484 | 0.34788 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | common_unequal | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 4 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 3.75 | 0.34777 | 0.32036 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-03 | 2026-02-09 10:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.1303 | 1.4024 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | baseline | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.32388 | 0.29907 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | unilateral_drift | TRUE | 2.725 | 1 | 3 | 5 | 3 | 5 | 2 | 1 | 2.7 | 2.275 | 2.275 | 2.7875 | 2.275 | 1.0153 | 1.2246 | 0.70139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | unilateral_step | TRUE | 2.4625 | 3 | 4 | 4 | 1 | 4 | 3 | 3 | 3.05 | 2.5375 | 2.5375 | 2.5375 | 2.5375 | 0.64589 | 0.74314 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | unilateral_freeze | TRUE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 4 | 4.4 | 4.05 | 4.05 | 4.05 | 3.7875 | 0.38303 | 0.37913 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | unilateral_spike | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.45228 | 0.50843 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.4888 | 1.8702 | 0.91667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.28415 | 0.30692 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | distribution_tail | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 3 | 4 | 4.25 | 3.9375 | 3.9375 | 3.675 | 3.9375 | 0.57812 | 0.71354 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | distribution_mixture | TRUE | 1.2125 | 4 | 5 | 4 | 3 | 4 | 5 | 3 | 4.05 | 3.7875 | 3.7875 | 4.05 | 3.525 | 0.48551 | 0.50362 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.20833 | 0.17129 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.20833 | 0.17129 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | common_unequal | FALSE | 1.5125 | 3 | 4 | 5 | 3 | 5 | 3 | 4 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 3.75 | 0.59261 | 0.70065 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-04 | 2026-02-13 15:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.8158 | 2.4245 | 0.90278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | baseline | FALSE | 1.4625 | 5 | 2 | 5 | 4 | 5 | 5 | 5 | 4.05 | 3.5375 | 3.5375 | 3.5375 | 3.5375 | 0.3928 | 0.44171 | 0.31944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | unilateral_drift | TRUE | 2.4625 | 4 | 1 | 4 | 3 | 4 | 4 | 4 | 3.05 | 2.5375 | 2.5375 | 2.5375 | 2.5375 | 0.51478 | 0.58018 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | unilateral_step | TRUE | 2.4625 | 5 | 2 | 3 | 1 | 3 | 5 | 5 | 3.05 | 2.5375 | 2.5375 | 2.5375 | 2.5375 | 0.33744 | 0.34482 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | unilateral_freeze | TRUE | 2.6875 | 1 | 4 | 3 | 4 | 3 | 1 | 2 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.825 | 1.0692 | 1.37 | 0.61806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | unilateral_spike | TRUE | 1.725 | 4 | 2 | 5 | 4 | 5 | 4 | 5 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.52918 | 0.65974 | 0.33333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | distribution_location | TRUE | 2.4 | 2 | 2 | 5 | 3 | 5 | 2 | 1 | 2.8 | 2.6 | 2.6 | 2.6 | 2.0875 | 0.95276 | 1.1064 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | distribution_scale | TRUE | 1.6125 | 5 | 2 | 4 | 4 | 4 | 5 | 5 | 3.85 | 3.3875 | 3.3875 | 3.3875 | 3.3875 | 0.32718 | 0.34159 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | distribution_tail | TRUE | 1.4625 | 5 | 2 | 5 | 4 | 5 | 5 | 5 | 4.05 | 3.5375 | 3.5375 | 3.5375 | 3.5375 | 0.30476 | 0.33664 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | distribution_mixture | TRUE | 0.95 | 5 | 5 | 3 | 4 | 3 | 5 | 4 | 4.4 | 4.05 | 4.05 | 4.05 | 3.7875 | 0.36563 | 0.36865 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | synchronous_switch | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.31011 | 0.31778 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | common_mode_drift | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.31011 | 0.31778 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | common_unequal | FALSE | 1.7625 | 5 | 2 | 4 | 3 | 4 | 5 | 5 | 3.65 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 0.33332 | 0.35183 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-05 | 2026-02-17 20:00 | opposite_direction | FALSE | 2.8375 | 2 | 1 | 5 | 3 | 5 | 2 | 2 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 0.81806 | 1.0069 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | baseline | FALSE | 1.3125 | 5 | 2 | 5 | 5 | 5 | 5 | 5 | 4.25 | 3.6875 | 3.6875 | 3.6875 | 3.6875 | 0.32639 | 0.34954 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | unilateral_drift | TRUE | 2.5375 | 2 | 1 | 5 | 5 | 5 | 2 | 2 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 0.95602 | 1.1721 | 0.63194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | unilateral_step | TRUE | 2.575 | 3 | 1 | 4 | 4 | 4 | 3 | 2 | 2.9 | 2.425 | 2.425 | 2.425 | 2.1625 | 0.72248 | 0.81525 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | unilateral_freeze | TRUE | 1.4375 | 4 | 3 | 3 | 5 | 3 | 4 | 4 | 3.75 | 3.5625 | 3.5625 | 3.5625 | 3.5625 | 0.4708 | 0.5393 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | unilateral_spike | TRUE | 1.3125 | 5 | 2 | 5 | 5 | 5 | 5 | 5 | 4.25 | 3.6875 | 3.6875 | 3.6875 | 3.6875 | 0.41043 | 0.49886 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | distribution_location | TRUE | 2.6125 | 1 | 2 | 5 | 5 | 5 | 1 | 1 | 2.85 | 2.3875 | 2.3875 | 2.3875 | 2.3875 | 1.6039 | 2.0112 | 0.99306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | distribution_scale | TRUE | 0.875 | 5 | 3 | 5 | 5 | 5 | 5 | 5 | 4.5 | 4.125 | 4.125 | 4.125 | 4.125 | 0.28597 | 0.30532 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | distribution_tail | TRUE | 1.1375 | 4 | 3 | 5 | 5 | 5 | 3 | 5 | 4.15 | 3.8625 | 3.8625 | 3.6 | 4.125 | 0.55165 | 0.72497 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | distribution_mixture | TRUE | 0.7375 | 5 | 4 | 4 | 4 | 4 | 5 | 4 | 4.35 | 4.2625 | 4.2625 | 4.2625 | 4 | 0.42206 | 0.43028 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | synchronous_switch | FALSE | 1.025 | 5 | 3 | 4 | 5 | 4 | 5 | 5 | 4.3 | 3.975 | 3.975 | 3.975 | 3.975 | 0.4278 | 0.49541 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | common_mode_drift | FALSE | 1.025 | 5 | 3 | 4 | 5 | 4 | 5 | 5 | 4.3 | 3.975 | 3.975 | 3.975 | 3.975 | 0.4278 | 0.49541 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | common_unequal | FALSE | 2.6875 | 2 | 1 | 4 | 5 | 4 | 3 | 2 | 2.75 | 2.3125 | 2.3125 | 2.575 | 2.3125 | 0.76469 | 0.88559 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-06 | 2026-02-22 01:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 5 | 4 | 5 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.1985 | 1.4652 | 0.79861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | baseline | FALSE | 1.75 | 5 | 1 | 5 | 5 | 5 | 5 | 5 | 4 | 3.25 | 3.25 | 3.25 | 3.25 | 0.35201 | 0.44779 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | unilateral_drift | TRUE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 2 | 2 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.8894 | 1.0934 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | unilateral_step | TRUE | 0.6625 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 4.45 | 4.3375 | 4.3375 | 4.3375 | 4.3375 | 0.50643 | 0.57554 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | unilateral_freeze | TRUE | 2.575 | 3 | 1 | 3 | 5 | 3 | 3 | 3 | 2.9 | 2.425 | 2.425 | 2.425 | 2.425 | 0.72286 | 0.88995 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | unilateral_spike | TRUE | 1.3125 | 5 | 2 | 5 | 5 | 5 | 4 | 5 | 4.25 | 3.6875 | 3.6875 | 3.425 | 3.6875 | 0.4001 | 0.54184 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | distribution_location | TRUE | 2.8 | 1 | 1 | 5 | 5 | 5 | 1 | 1 | 2.6 | 2.2 | 2.2 | 2.2 | 2.2 | 1.1857 | 1.5364 | 0.65972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | distribution_scale | TRUE | 1.025 | 5 | 3 | 4 | 5 | 4 | 5 | 5 | 4.3 | 3.975 | 3.975 | 3.975 | 3.975 | 0.24842 | 0.26126 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | distribution_tail | TRUE | 1.3125 | 5 | 2 | 5 | 5 | 5 | 4 | 5 | 4.25 | 3.6875 | 3.6875 | 3.425 | 3.6875 | 0.38465 | 0.54386 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | distribution_mixture | TRUE | 0.9875 | 5 | 4 | 3 | 5 | 3 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.3493 | 0.39699 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | synchronous_switch | FALSE | 0.875 | 5 | 3 | 5 | 5 | 5 | 5 | 5 | 4.5 | 4.125 | 4.125 | 4.125 | 4.125 | 0.31135 | 0.36614 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | common_mode_drift | FALSE | 0.875 | 5 | 3 | 5 | 5 | 5 | 5 | 5 | 4.5 | 4.125 | 4.125 | 4.125 | 4.125 | 0.31135 | 0.36614 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | common_unequal | FALSE | 0.7 | 4 | 4 | 5 | 5 | 5 | 4 | 4 | 4.4 | 4.3 | 4.3 | 4.3 | 4.3 | 0.49917 | 0.58657 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-07 | 2026-02-26 07:00 | opposite_direction | FALSE | 2.425 | 1 | 3 | 5 | 5 | 5 | 1 | 1 | 3.1 | 2.575 | 2.575 | 2.575 | 2.575 | 1.6373 | 2.1455 | 0.875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | baseline | FALSE | 2.1 | 2 | 2 | 5 | 5 | 5 | 2 | 2 | 3.2 | 2.9 | 2.9 | 2.9 | 2.9 | 0.84437 | 0.99988 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | unilateral_drift | TRUE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.39043 | 0.43312 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | unilateral_step | TRUE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 4 | 4.6 | 4.45 | 4.45 | 4.45 | 4.1875 | 0.30327 | 0.26934 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | unilateral_freeze | TRUE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.0829 | 1.3558 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | unilateral_spike | TRUE | 2.1 | 2 | 2 | 5 | 5 | 5 | 2 | 2 | 3.2 | 2.9 | 2.9 | 2.9 | 2.9 | 0.92169 | 1.1473 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | distribution_location | TRUE | 2.1 | 2 | 2 | 5 | 5 | 5 | 2 | 2 | 3.2 | 2.9 | 2.9 | 2.9 | 2.9 | 0.83708 | 0.97383 | 0.63194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | distribution_scale | TRUE | 1.55 | 3 | 3 | 5 | 4 | 5 | 3 | 3 | 3.6 | 3.45 | 3.45 | 3.45 | 3.45 | 0.63172 | 0.73805 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | distribution_tail | TRUE | 2.1 | 2 | 2 | 5 | 5 | 5 | 2 | 3 | 3.2 | 2.9 | 2.9 | 2.9 | 3.1625 | 0.82759 | 1.0321 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | distribution_mixture | TRUE | 1.4 | 4 | 4 | 3 | 4 | 3 | 5 | 2 | 3.8 | 3.6 | 3.6 | 3.8625 | 2.825 | 0.52774 | 0.51383 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | synchronous_switch | FALSE | 0.85 | 4 | 4 | 5 | 4 | 5 | 4 | 3 | 4.2 | 4.15 | 4.15 | 4.15 | 3.6375 | 0.54421 | 0.5598 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | common_mode_drift | FALSE | 0.85 | 4 | 4 | 5 | 4 | 5 | 4 | 3 | 4.2 | 4.15 | 4.15 | 4.15 | 3.6375 | 0.54421 | 0.5598 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | common_unequal | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.16676 | 0.18071 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-08 | 2026-03-02 12:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 4 | 5 | 4 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.4764 | 1.8171 | 0.96528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | baseline | FALSE | 1.65 | 4 | 4 | 5 | 2 | 5 | 4 | 3 | 3.8 | 3.35 | 3.35 | 3.35 | 3.0875 | 0.52178 | 0.57333 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | unilateral_drift | TRUE | 2.875 | 1 | 3 | 5 | 2 | 5 | 1 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 1.4082 | 1.7636 | 0.875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | unilateral_step | TRUE | 2.175 | 2 | 4 | 5 | 2 | 5 | 2 | 1 | 3.1 | 2.825 | 2.825 | 2.825 | 2.3125 | 0.95704 | 1.1321 | 0.69444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | unilateral_freeze | TRUE | 2.2875 | 2 | 5 | 3 | 2 | 3 | 2 | 1 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.2 | 0.84163 | 0.93976 | 0.69444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | unilateral_spike | TRUE | 1.9125 | 3 | 4 | 5 | 2 | 5 | 3 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.35 | 0.63118 | 0.76493 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | distribution_location | TRUE | 2.6875 | 1 | 4 | 5 | 2 | 5 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 1.802 | 2.4154 | 0.88194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | distribution_scale | TRUE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 4 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.35 | 0.44224 | 0.48706 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | distribution_tail | TRUE | 1.9875 | 2 | 5 | 5 | 2 | 5 | 2 | 3 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.275 | 0.81793 | 1.0438 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | distribution_mixture | TRUE | 1.7625 | 4 | 5 | 3 | 2 | 3 | 4 | 3 | 3.65 | 3.2375 | 3.2375 | 3.2375 | 2.975 | 0.52222 | 0.55555 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.36024 | 0.36428 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.36024 | 0.36428 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | common_unequal | FALSE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.0999 | 1.3285 | 0.75694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-09 | 2026-03-06 17:00 | opposite_direction | FALSE | 3.2125 | 1 | 2 | 4 | 2 | 4 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 1.6505 | 2.0842 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | baseline | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.19339 | 0.20658 | 0.17361 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | unilateral_drift | TRUE | 2.875 | 1 | 3 | 5 | 2 | 5 | 1 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 1.1714 | 1.3968 | 0.83333 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | unilateral_step | TRUE | 2.55 | 2 | 2 | 5 | 2 | 5 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.92707 | 1.1146 | 0.64583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | unilateral_freeze | TRUE | 1.4625 | 4 | 5 | 5 | 2 | 5 | 4 | 2 | 4.05 | 3.5375 | 3.5375 | 3.5375 | 3.0125 | 0.54335 | 0.53985 | 0.54861 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | unilateral_spike | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.28207 | 0.359 | 0.16667 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.3659 | 1.6468 | 0.94444 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | distribution_scale | TRUE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 5 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.6125 | 0.29468 | 0.29206 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | distribution_tail | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 4 | 5 | 4.4 | 3.8 | 3.8 | 3.5375 | 3.8 | 0.44074 | 0.58179 | 0.22917 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | distribution_mixture | TRUE | 1.7625 | 4 | 5 | 3 | 2 | 3 | 5 | 3 | 3.65 | 3.2375 | 3.2375 | 3.5 | 2.975 | 0.4849 | 0.51186 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.22073 | 0.21511 | 0.22917 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.22073 | 0.21511 | 0.22917 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | common_unequal | FALSE | 2.175 | 2 | 4 | 5 | 2 | 5 | 3 | 1 | 3.1 | 2.825 | 2.825 | 3.0875 | 2.3125 | 0.79922 | 0.89684 | 0.65278 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-10 | 2026-03-10 22:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.9687 | 2.6468 | 0.95139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | baseline | FALSE | 0.55 | 5 | 5 | 4 | 4 | 4 | 5 | 4 | 4.6 | 4.45 | 4.45 | 4.45 | 4.1875 | 0.41999 | 0.44998 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | unilateral_drift | TRUE | 2.575 | 1 | 3 | 5 | 4 | 5 | 1 | 1 | 2.9 | 2.425 | 2.425 | 2.425 | 2.425 | 1.114 | 1.366 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | unilateral_step | TRUE | 1.5125 | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 3.4875 | 0.7038 | 0.83966 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | unilateral_freeze | TRUE | 1.2125 | 4 | 5 | 3 | 4 | 3 | 4 | 4 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.7875 | 0.51472 | 0.58009 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | unilateral_spike | TRUE | 0.8125 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4.25 | 4.1875 | 4.1875 | 4.1875 | 4.1875 | 0.52789 | 0.64833 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | distribution_location | TRUE | 2.35 | 1 | 5 | 4 | 4 | 4 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.9067 | 2.525 | 0.97917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | distribution_scale | TRUE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.31904 | 0.32804 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | distribution_tail | TRUE | 1.175 | 3 | 5 | 5 | 4 | 5 | 3 | 4 | 4.1 | 3.825 | 3.825 | 3.825 | 4.3375 | 0.65865 | 0.84775 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | distribution_mixture | TRUE | 1.2125 | 4 | 5 | 3 | 4 | 3 | 4 | 2 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.0125 | 0.5662 | 0.54552 | 0.59722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.21395 | 0.25935 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.21395 | 0.25935 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | common_unequal | FALSE | 1.175 | 3 | 5 | 5 | 4 | 5 | 3 | 3 | 4.1 | 3.825 | 3.825 | 3.825 | 3.825 | 0.71565 | 0.86867 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-11 | 2026-03-15 03:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 5 | 4 | 5 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.7007 | 2.228 | 0.90972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | baseline | FALSE | 1.6625 | 3 | 4 | 4 | 3 | 4 | 3 | 3 | 3.45 | 3.3375 | 3.3375 | 3.3375 | 3.3375 | 0.63305 | 0.71712 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | unilateral_drift | TRUE | 2.4625 | 4 | 1 | 5 | 2 | 5 | 4 | 4 | 3.05 | 2.5375 | 2.5375 | 2.5375 | 2.5375 | 0.51065 | 0.59646 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | unilateral_step | TRUE | 1.9125 | 5 | 2 | 4 | 2 | 4 | 5 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 2.825 | 0.36525 | 0.32635 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | unilateral_freeze | TRUE | 1.8125 | 3 | 4 | 3 | 3 | 3 | 4 | 2 | 3.25 | 3.1875 | 3.1875 | 3.45 | 2.675 | 0.63722 | 0.68703 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | unilateral_spike | TRUE | 1.6625 | 3 | 4 | 4 | 3 | 4 | 3 | 3 | 3.45 | 3.3375 | 3.3375 | 3.3375 | 3.3375 | 0.71976 | 0.87553 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | distribution_location | TRUE | 1.875 | 2 | 4 | 4 | 5 | 4 | 2 | 1 | 3.5 | 3.125 | 3.125 | 3.125 | 2.6125 | 0.92234 | 1.065 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | distribution_scale | TRUE | 1.25 | 4 | 4 | 5 | 3 | 5 | 3 | 4 | 4 | 3.75 | 3.75 | 3.4875 | 3.75 | 0.58394 | 0.71397 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | distribution_tail | TRUE | 1.6625 | 3 | 4 | 4 | 3 | 4 | 3 | 4 | 3.45 | 3.3375 | 3.3375 | 3.3375 | 3.6 | 0.62006 | 0.76492 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | distribution_mixture | TRUE | 1.2125 | 4 | 5 | 4 | 3 | 4 | 5 | 3 | 4.05 | 3.7875 | 3.7875 | 4.05 | 3.525 | 0.4772 | 0.47589 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | synchronous_switch | FALSE | 1.65 | 4 | 4 | 5 | 2 | 5 | 4 | 5 | 3.8 | 3.35 | 3.35 | 3.35 | 3.6125 | 0.52431 | 0.64237 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | common_mode_drift | FALSE | 1.65 | 4 | 4 | 5 | 2 | 5 | 4 | 5 | 3.8 | 3.35 | 3.35 | 3.35 | 3.6125 | 0.52431 | 0.64237 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | common_unequal | FALSE | 1.7625 | 5 | 2 | 5 | 2 | 5 | 5 | 5 | 3.65 | 3.2375 | 3.2375 | 3.2375 | 3.2375 | 0.25816 | 0.29601 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-12 | 2026-03-19 08:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 2 | 1 | 2 | 1.75 | 1.75 | 2.0125 | 1.75 | 0.99405 | 1.166 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | baseline | FALSE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.1872 | 1.5018 | 0.71528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | unilateral_drift | TRUE | 2.05 | 1 | 5 | 5 | 5 | 5 | 1 | 1 | 3.6 | 2.95 | 2.95 | 2.95 | 2.95 | 1.3053 | 1.6801 | 0.74306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | unilateral_step | TRUE | 1.6875 | 2 | 5 | 4 | 5 | 4 | 2 | 1 | 3.75 | 3.3125 | 3.3125 | 3.3125 | 2.8 | 0.94132 | 1.092 | 0.71528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | unilateral_freeze | TRUE | 3.25 | 1 | 1 | 2 | 5 | 2 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.2868 | 1.6679 | 0.71528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | unilateral_spike | TRUE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.3164 | 1.731 | 0.69444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | distribution_location | TRUE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 2.7419 | 3.9032 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | distribution_scale | TRUE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.0814 | 1.3347 | 0.70139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | distribution_tail | TRUE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.4984 | 2.0205 | 0.71528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | distribution_mixture | TRUE | 0.9875 | 5 | 4 | 3 | 5 | 3 | 5 | 3 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 3.4875 | 0.45738 | 0.44749 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | synchronous_switch | FALSE | 0.85 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 4.2 | 4.15 | 4.15 | 4.15 | 4.15 | 0.47507 | 0.52327 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | common_mode_drift | FALSE | 0.85 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 4.2 | 4.15 | 4.15 | 4.15 | 4.15 | 0.47507 | 0.52327 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | common_unequal | FALSE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 2 | 2 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.88089 | 1.0376 | 0.64583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-13 | 2026-03-23 14:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 2.7593 | 3.9322 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | baseline | FALSE | 1.2125 | 4 | 5 | 4 | 3 | 4 | 4 | 3 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.525 | 0.56277 | 0.60924 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | unilateral_drift | TRUE | 2.5375 | 1 | 4 | 5 | 3 | 5 | 2 | 1 | 2.95 | 2.4625 | 2.4625 | 2.975 | 2.4625 | 0.98717 | 1.1962 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | unilateral_step | TRUE | 2.175 | 2 | 4 | 4 | 3 | 4 | 3 | 2 | 3.1 | 2.825 | 2.825 | 3.3375 | 2.825 | 0.74813 | 0.858 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | unilateral_freeze | TRUE | 1.625 | 3 | 5 | 3 | 3 | 3 | 3 | 2 | 3.5 | 3.375 | 3.375 | 3.375 | 2.8625 | 0.68388 | 0.75092 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | unilateral_spike | TRUE | 1.475 | 3 | 5 | 4 | 3 | 4 | 3 | 3 | 3.7 | 3.525 | 3.525 | 3.525 | 3.525 | 0.63561 | 0.74453 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 4 | 3 | 4 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.7341 | 2.2884 | 0.90278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.45385 | 0.4879 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | distribution_tail | TRUE | 1.8375 | 2 | 5 | 5 | 3 | 5 | 2 | 3 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 3.675 | 0.77297 | 0.94569 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | distribution_mixture | TRUE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 4 | 4.4 | 4.05 | 4.05 | 4.05 | 3.7875 | 0.43968 | 0.45966 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.24423 | 0.23576 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.24423 | 0.23576 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | common_unequal | FALSE | 1.325 | 3 | 5 | 5 | 3 | 5 | 4 | 3 | 3.9 | 3.675 | 3.675 | 3.9375 | 3.675 | 0.60098 | 0.69608 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-14 | 2026-03-27 19:00 | opposite_direction | FALSE | 2.9125 | 1 | 2 | 5 | 3 | 5 | 1 | 1 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.0875 | 1.4386 | 1.7959 | 0.90278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | baseline | FALSE | 1.025 | 5 | 3 | 4 | 5 | 4 | 5 | 4 | 4.3 | 3.975 | 3.975 | 3.975 | 3.7125 | 0.42441 | 0.46661 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | unilateral_drift | TRUE | 2.175 | 2 | 4 | 5 | 2 | 5 | 2 | 2 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.84655 | 0.985 | 0.63889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | unilateral_step | TRUE | 1.3625 | 3 | 4 | 4 | 5 | 4 | 4 | 3 | 3.85 | 3.6375 | 3.6375 | 4.15 | 3.6375 | 0.59045 | 0.65075 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | unilateral_freeze | TRUE | 1.7 | 3 | 3 | 3 | 5 | 3 | 3 | 4 | 3.4 | 3.3 | 3.3 | 3.3 | 3.5625 | 0.66049 | 0.85544 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | unilateral_spike | TRUE | 1.2875 | 4 | 3 | 4 | 5 | 4 | 3 | 5 | 3.95 | 3.7125 | 3.7125 | 3.45 | 3.975 | 0.56092 | 0.71265 | 0.33333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | distribution_location | TRUE | 3.025 | 1 | 3 | 4 | 2 | 4 | 1 | 1 | 2.3 | 1.975 | 1.975 | 1.975 | 1.975 | 1.7384 | 2.3094 | 0.88194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | distribution_scale | TRUE | 1.025 | 5 | 3 | 4 | 5 | 4 | 5 | 5 | 4.3 | 3.975 | 3.975 | 3.975 | 3.975 | 0.28709 | 0.3257 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | distribution_tail | TRUE | 1.3625 | 3 | 4 | 4 | 5 | 4 | 3 | 5 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 4.4125 | 0.62067 | 0.86315 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | distribution_mixture | TRUE | 1.0625 | 4 | 5 | 3 | 5 | 3 | 5 | 3 | 4.25 | 3.9375 | 3.9375 | 4.2 | 3.675 | 0.50226 | 0.51302 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.22021 | 0.20498 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.22021 | 0.20498 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | common_unequal | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 4 | 4.4 | 3.8 | 3.8 | 3.8 | 3.5375 | 0.44434 | 0.48593 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-15 | 2026-04-01 | opposite_direction | FALSE | 2.95 | 1 | 1 | 5 | 4 | 5 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.5967 | 2.0269 | 0.95139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | baseline | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 4 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 3.75 | 0.4 | 0.42592 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | unilateral_drift | TRUE | 1.8375 | 3 | 2 | 5 | 5 | 5 | 3 | 4 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 3.425 | 0.64384 | 0.78603 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | unilateral_step | TRUE | 1.725 | 5 | 3 | 4 | 2 | 4 | 5 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.0125 | 0.45105 | 0.46471 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | unilateral_freeze | TRUE | 1.55 | 4 | 4 | 3 | 3 | 3 | 4 | 3 | 3.6 | 3.45 | 3.45 | 3.45 | 3.1875 | 0.52033 | 0.56629 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | unilateral_spike | TRUE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 4 | 5 | 4.35 | 4.0125 | 4.0125 | 3.75 | 4.0125 | 0.45017 | 0.53268 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | distribution_location | TRUE | 2.5375 | 1 | 4 | 5 | 3 | 5 | 1 | 1 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 1.239 | 1.5419 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | distribution_scale | TRUE | 0.4375 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 4.75 | 4.5625 | 4.5625 | 4.5625 | 4.5625 | 0.33774 | 0.38235 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | distribution_tail | TRUE | 0.4375 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 4.75 | 4.5625 | 4.5625 | 4.5625 | 4.5625 | 0.40103 | 0.49709 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | distribution_mixture | TRUE | 0.4 | 5 | 5 | 4 | 5 | 4 | 5 | 4 | 4.8 | 4.6 | 4.6 | 4.6 | 4.3375 | 0.44456 | 0.44926 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.24554 | 0.23794 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.24554 | 0.23794 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | common_unequal | FALSE | 1.025 | 5 | 3 | 4 | 5 | 4 | 5 | 4 | 4.3 | 3.975 | 3.975 | 3.975 | 3.7125 | 0.40558 | 0.43986 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-16 | 2026-04-05 05:00 | opposite_direction | FALSE | 2.8 | 1 | 1 | 5 | 5 | 5 | 2 | 1 | 2.6 | 2.2 | 2.2 | 2.4625 | 2.2 | 1.0194 | 1.236 | 0.69444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | baseline | FALSE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.3119 | 0.39484 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | unilateral_drift | TRUE | 2.175 | 2 | 4 | 4 | 3 | 4 | 2 | 2 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.80361 | 0.93195 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | unilateral_step | TRUE | 1.6625 | 3 | 4 | 4 | 3 | 4 | 4 | 3 | 3.45 | 3.3375 | 3.3375 | 3.6 | 3.3375 | 0.60581 | 0.67635 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | unilateral_freeze | TRUE | 2.25 | 3 | 3 | 2 | 4 | 2 | 3 | 4 | 3 | 2.75 | 2.75 | 2.75 | 3.0125 | 0.70267 | 0.88871 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | unilateral_spike | TRUE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4.55 | 4.4125 | 4.4125 | 4.15 | 4.4125 | 0.42967 | 0.60038 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | distribution_location | TRUE | 2.3875 | 1 | 4 | 4 | 5 | 4 | 1 | 1 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 1.7329 | 2.2677 | 0.93056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | distribution_scale | TRUE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.21621 | 0.2585 | 0.15278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | distribution_tail | TRUE | 0.85 | 4 | 4 | 4 | 5 | 4 | 3 | 5 | 4.2 | 4.15 | 4.15 | 3.6375 | 4.4125 | 0.50619 | 0.70476 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | distribution_mixture | TRUE | 1.4 | 4 | 4 | 3 | 4 | 3 | 5 | 3 | 3.8 | 3.6 | 3.6 | 3.8625 | 3.3375 | 0.46359 | 0.46247 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.21216 | 0.14527 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.21216 | 0.14527 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | common_unequal | FALSE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 5 | 4 | 4.25 | 3.9375 | 3.9375 | 4.2 | 3.9375 | 0.45782 | 0.49915 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-17 | 2026-04-09 10:00 | opposite_direction | FALSE | 3.0625 | 1 | 2 | 4 | 3 | 4 | 1 | 1 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 1.4485 | 1.7752 | 0.95833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | baseline | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.34435 | 0.43503 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | unilateral_drift | TRUE | 2.0625 | 2 | 3 | 4 | 5 | 4 | 2 | 2 | 3.25 | 2.9375 | 2.9375 | 2.9375 | 2.9375 | 0.87612 | 1.0898 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | unilateral_step | TRUE | 1.55 | 3 | 3 | 4 | 5 | 4 | 3 | 3 | 3.6 | 3.45 | 3.45 | 3.45 | 3.45 | 0.688 | 0.80407 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | unilateral_freeze | TRUE | 0 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4.4875 | 5 | 0.44952 | 0.56864 | 0.27083 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | unilateral_spike | TRUE | 0 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4.4875 | 5 | 0.41422 | 0.56537 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | distribution_location | TRUE | 2.05 | 1 | 5 | 5 | 5 | 5 | 1 | 1 | 3.6 | 2.95 | 2.95 | 2.95 | 2.95 | 1.4179 | 1.9141 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | distribution_scale | TRUE | 0.6625 | 4 | 5 | 4 | 5 | 4 | 3 | 5 | 4.45 | 4.3375 | 4.3375 | 3.825 | 4.6 | 0.5354 | 0.72567 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | distribution_tail | TRUE | 0.4 | 5 | 5 | 4 | 5 | 4 | 4 | 5 | 4.8 | 4.6 | 4.6 | 4.3375 | 4.6 | 0.43826 | 0.61006 | 0.18056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | distribution_mixture | TRUE | 0.9875 | 5 | 4 | 3 | 5 | 3 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.41846 | 0.50299 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.11416 | 0.12082 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.11416 | 0.12082 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | common_unequal | FALSE | 0.5125 | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 4.65 | 4.4875 | 4.4875 | 4.4875 | 5 | 0.50223 | 0.6102 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP11 | PAIR_ORP11-18 | 2026-04-13 16:00 | opposite_direction | FALSE | 2.6125 | 1 | 2 | 5 | 5 | 5 | 1 | 1 | 2.85 | 2.3875 | 2.3875 | 2.3875 | 2.3875 | 1.1755 | 1.4499 | 0.76389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | baseline | FALSE | 2.9875 | 1 | 4 | 4 | 1 | 4 | 1 | 2 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.275 | 1.1083 | 1.4351 | 0.61806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | unilateral_drift | TRUE | 3.5125 | 1 | 2 | 3 | 1 | 3 | 1 | 1 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 1.4875 | 1.2792 | 1.5996 | 0.79861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | unilateral_step | TRUE | 3.475 | 1 | 3 | 2 | 1 | 2 | 2 | 1 | 1.7 | 1.525 | 1.525 | 1.7875 | 1.525 | 1.0496 | 1.2632 | 0.72917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | unilateral_freeze | TRUE | 2.3875 | 2 | 5 | 5 | 1 | 5 | 2 | 1 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 2.35 | 0.93522 | 1.0587 | 0.75 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | unilateral_spike | TRUE | 2.9875 | 1 | 4 | 4 | 1 | 4 | 1 | 2 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.275 | 1.2527 | 1.685 | 0.60417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | distribution_location | TRUE | 2.9875 | 1 | 4 | 4 | 1 | 4 | 1 | 1 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 2.1752 | 3.0559 | 0.85417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | distribution_scale | TRUE | 3.1375 | 1 | 4 | 3 | 1 | 3 | 1 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.125 | 1.1739 | 1.5815 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | distribution_tail | TRUE | 2.9875 | 1 | 4 | 4 | 1 | 4 | 1 | 2 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.275 | 1.3998 | 1.9071 | 0.63889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | distribution_mixture | TRUE | 2.575 | 3 | 5 | 2 | 1 | 2 | 3 | 4 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.69448 | 0.87044 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.3971 | 0.4674 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.3971 | 0.4674 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | common_unequal | FALSE | 2.725 | 2 | 4 | 4 | 1 | 4 | 2 | 2 | 2.7 | 2.275 | 2.275 | 2.275 | 2.275 | 0.84511 | 1.0242 | 0.57639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-01 | 2026-02-01 | opposite_direction | FALSE | 3.55 | 1 | 1 | 4 | 1 | 4 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.3841 | 1.7374 | 0.85417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | baseline | FALSE | 1.8125 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3.25 | 3.1875 | 3.1875 | 3.1875 | 3.1875 | 0.63016 | 0.75397 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | unilateral_drift | TRUE | 3.55 | 1 | 1 | 2 | 3 | 2 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.1225 | 1.3847 | 0.72917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | unilateral_step | TRUE | 3.0625 | 2 | 3 | 1 | 3 | 1 | 3 | 2 | 2.25 | 1.9375 | 1.9375 | 2.2 | 1.9375 | 0.74421 | 0.85147 | 0.58333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | unilateral_freeze | TRUE | 2.5375 | 1 | 4 | 5 | 3 | 5 | 1 | 1 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 1.2158 | 1.5911 | 0.65278 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | unilateral_spike | TRUE | 2.325 | 2 | 4 | 3 | 3 | 3 | 2 | 3 | 2.9 | 2.675 | 2.675 | 2.675 | 3.1875 | 0.82506 | 1.0695 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | distribution_location | TRUE | 2.8375 | 1 | 4 | 3 | 3 | 3 | 1 | 1 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 1.7038 | 2.2564 | 0.875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | distribution_scale | TRUE | 2.6625 | 2 | 3 | 2 | 3 | 2 | 2 | 3 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.6 | 0.77977 | 0.98943 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | distribution_tail | TRUE | 2.325 | 2 | 4 | 3 | 3 | 3 | 2 | 3 | 2.9 | 2.675 | 2.675 | 2.675 | 3.1875 | 0.92 | 1.2046 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | distribution_mixture | TRUE | 2.425 | 3 | 5 | 1 | 3 | 1 | 3 | 3 | 3.1 | 2.575 | 2.575 | 2.575 | 2.575 | 0.68419 | 0.81625 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.21097 | 0.2405 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.21097 | 0.2405 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | common_unequal | FALSE | 1.85 | 3 | 3 | 4 | 3 | 4 | 3 | 2 | 3.2 | 3.15 | 3.15 | 3.15 | 2.6375 | 0.70435 | 0.80355 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-02 | 2026-02-05 05:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.4231 | 1.8487 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | baseline | FALSE | 1.6875 | 2 | 5 | 4 | 5 | 4 | 2 | 1 | 3.75 | 3.3125 | 3.3125 | 3.3125 | 2.8 | 0.95458 | 1.1095 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | unilateral_drift | TRUE | 2.725 | 1 | 3 | 3 | 5 | 3 | 1 | 1 | 2.7 | 2.275 | 2.275 | 2.275 | 2.275 | 1.2923 | 1.5936 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | unilateral_step | TRUE | 2.725 | 1 | 3 | 3 | 5 | 3 | 2 | 1 | 2.7 | 2.275 | 2.275 | 2.7875 | 2.275 | 0.9873 | 1.1085 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | unilateral_freeze | TRUE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 2 | 1 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 2.95 | 0.90438 | 0.91934 | 0.88194 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | unilateral_spike | TRUE | 2.2 | 1 | 5 | 4 | 5 | 4 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.0831 | 1.333 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 4 | 5 | 4 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.934 | 2.6308 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | distribution_scale | TRUE | 2.35 | 1 | 5 | 3 | 5 | 3 | 2 | 2 | 3.2 | 2.65 | 2.65 | 3.1625 | 3.1625 | 1.0046 | 1.253 | 0.63194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | distribution_tail | TRUE | 2.05 | 1 | 5 | 5 | 5 | 5 | 1 | 1 | 3.6 | 2.95 | 2.95 | 2.95 | 2.95 | 1.2901 | 1.6456 | 0.75694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | distribution_mixture | TRUE | 2.025 | 3 | 5 | 2 | 3 | 2 | 3 | 3 | 3.3 | 2.975 | 2.975 | 2.975 | 2.975 | 0.70067 | 0.86686 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4.4875 | 0.38823 | 0.38779 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4.4875 | 0.38823 | 0.38779 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | common_unequal | FALSE | 1.875 | 2 | 4 | 4 | 5 | 4 | 2 | 1 | 3.5 | 3.125 | 3.125 | 3.125 | 2.6125 | 0.93571 | 1.0966 | 0.69444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-03 | 2026-02-09 10:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.558 | 2.0271 | 0.85417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | baseline | FALSE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 3 | 2 | 2.95 | 2.4625 | 2.4625 | 2.725 | 2.4625 | 0.75313 | 0.88484 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | unilateral_drift | TRUE | 3.1 | 2 | 2 | 1 | 4 | 1 | 2 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.6375 | 0.95635 | 1.0291 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | unilateral_step | TRUE | 2.65 | 3 | 3 | 1 | 4 | 1 | 3 | 2 | 2.8 | 2.35 | 2.35 | 2.35 | 2.0875 | 0.73076 | 0.86145 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | unilateral_freeze | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 3.0006 | 4.4362 | 0.84722 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | unilateral_spike | TRUE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 2 | 2 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 0.97029 | 1.2514 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | distribution_location | TRUE | 2.95 | 1 | 5 | 1 | 3 | 1 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.8271 | 2.3785 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | distribution_scale | TRUE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 3 | 3 | 2.95 | 2.4625 | 2.4625 | 2.725 | 2.725 | 0.7397 | 0.8856 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | distribution_tail | TRUE | 2.8 | 1 | 5 | 1 | 4 | 1 | 1 | 3 | 2.6 | 2.2 | 2.2 | 2.2 | 2.725 | 1.0271 | 1.3785 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | distribution_mixture | TRUE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 2 | 3 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.725 | 0.81049 | 1.0036 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.27572 | 0.22806 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 4 | 4.6 | 4.2 | 4.2 | 4.2 | 3.9375 | 0.27572 | 0.22806 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | common_unequal | FALSE | 1.2875 | 5 | 4 | 3 | 3 | 3 | 5 | 4 | 3.95 | 3.7125 | 3.7125 | 3.7125 | 3.45 | 0.42898 | 0.46496 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-04 | 2026-02-13 15:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.2461 | 1.4842 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | baseline | FALSE | 2.6875 | 3 | 2 | 1 | 5 | 1 | 3 | 3 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 0.65479 | 0.77651 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | unilateral_drift | TRUE | 3.2125 | 1 | 2 | 1 | 5 | 1 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 2.5136 | 3.5227 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | unilateral_step | TRUE | 3.2125 | 1 | 2 | 1 | 5 | 1 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 1.7182 | 2.2711 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | unilateral_freeze | TRUE | 2.3875 | 1 | 4 | 4 | 5 | 4 | 1 | 1 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 5.9295 | 9.2898 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | unilateral_spike | TRUE | 2.95 | 2 | 2 | 1 | 5 | 1 | 2 | 3 | 2.4 | 2.05 | 2.05 | 2.05 | 2.3125 | 0.89329 | 1.1601 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | distribution_location | TRUE | 3.2125 | 1 | 2 | 1 | 5 | 1 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 2.342 | 3.2367 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | distribution_scale | TRUE | 2.6875 | 3 | 2 | 1 | 5 | 1 | 3 | 3 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 0.67397 | 0.80383 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | distribution_tail | TRUE | 3.2125 | 1 | 2 | 1 | 5 | 1 | 1 | 2 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 2.05 | 1.1411 | 1.536 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | distribution_mixture | TRUE | 2.3875 | 2 | 5 | 1 | 5 | 1 | 2 | 2 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 2.6125 | 0.81085 | 0.95327 | 0.59722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | synchronous_switch | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 4 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.2 | 0.31343 | 0.28628 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | common_mode_drift | FALSE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 4 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.2 | 0.31343 | 0.28628 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | common_unequal | FALSE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.2503 | 1.4681 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-05 | 2026-02-17 20:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9729 | 2.6216 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | baseline | FALSE | 2.575 | 3 | 5 | 1 | 2 | 1 | 3 | 4 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.64636 | 0.83652 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | unilateral_drift | TRUE | 3.5125 | 1 | 2 | 1 | 3 | 1 | 1 | 1 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 1.4875 | 1.1358 | 1.3745 | 0.77778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | unilateral_step | TRUE | 3.8125 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.1875 | 1.1875 | 1.1875 | 1.1875 | 1.0315 | 1.2747 | 0.66667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | unilateral_freeze | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.3999 | 1.8887 | 0.66667 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | unilateral_spike | TRUE | 2.8375 | 2 | 5 | 1 | 2 | 1 | 2 | 4 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.6875 | 0.88014 | 1.2215 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | distribution_location | TRUE | 2.95 | 1 | 5 | 1 | 3 | 1 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.884 | 2.5335 | 0.90972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | distribution_scale | TRUE | 2.575 | 3 | 5 | 1 | 2 | 1 | 2 | 4 | 2.9 | 2.425 | 2.425 | 2.1625 | 2.6875 | 0.7032 | 0.91275 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | distribution_tail | TRUE | 3.1 | 1 | 5 | 1 | 2 | 1 | 1 | 4 | 2.2 | 1.9 | 1.9 | 1.9 | 2.6875 | 1.0518 | 1.4799 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | distribution_mixture | TRUE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 2 | 2 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 0.78936 | 0.95912 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.19095 | 0.2025 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.19095 | 0.2025 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | common_unequal | FALSE | 1.4 | 4 | 4 | 3 | 4 | 3 | 4 | 3 | 3.8 | 3.6 | 3.6 | 3.6 | 3.3375 | 0.58096 | 0.62567 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-06 | 2026-02-22 01:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.3314 | 1.6032 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | baseline | FALSE | 3.25 | 2 | 2 | 1 | 3 | 1 | 2 | 3 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 0.74332 | 0.94257 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | unilateral_drift | TRUE | 3.7 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.0793 | 1.2895 | 0.76389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | unilateral_step | TRUE | 3.7375 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 1.35 | 1.2625 | 1.2625 | 1.525 | 1.2625 | 0.76239 | 0.89565 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | unilateral_freeze | TRUE | 2.5375 | 1 | 4 | 5 | 3 | 5 | 1 | 1 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 3.0371 | 4.5249 | 0.80556 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | unilateral_spike | TRUE | 3.25 | 2 | 2 | 1 | 3 | 1 | 2 | 4 | 2 | 1.75 | 1.75 | 1.75 | 2.275 | 0.92708 | 1.2535 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | distribution_location | TRUE | 3.5125 | 1 | 2 | 1 | 3 | 1 | 1 | 1 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 1.4875 | 1.7759 | 2.3672 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | distribution_scale | TRUE | 3.4375 | 2 | 1 | 1 | 3 | 1 | 2 | 3 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.825 | 0.79286 | 1.002 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | distribution_tail | TRUE | 3.5125 | 1 | 2 | 1 | 3 | 1 | 1 | 4 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 2.275 | 1.023 | 1.4366 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | distribution_mixture | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 3 | 2.5 | 2.125 | 2.125 | 2.125 | 2.3875 | 0.75874 | 0.93586 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.21666 | 0.24535 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.21666 | 0.24535 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | common_unequal | FALSE | 2.8 | 3 | 3 | 3 | 1 | 3 | 4 | 3 | 2.6 | 2.2 | 2.2 | 2.4625 | 2.2 | 0.60884 | 0.6814 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-07 | 2026-02-26 07:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 4 | 1 | 4 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.1976 | 1.459 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | baseline | FALSE | 2.85 | 2 | 2 | 2 | 3 | 2 | 2 | 3 | 2.2 | 2.15 | 2.15 | 2.15 | 2.4125 | 0.77737 | 0.98081 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | unilateral_drift | TRUE | 2.875 | 1 | 3 | 2 | 5 | 2 | 1 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 1.3723 | 1.764 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | unilateral_step | TRUE | 2.9875 | 1 | 4 | 2 | 3 | 2 | 2 | 1 | 2.35 | 2.0125 | 2.0125 | 2.525 | 2.0125 | 1.0063 | 1.1958 | 0.72222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | unilateral_freeze | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.2229 | 1.4827 | 0.83333 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | unilateral_spike | TRUE | 2.6625 | 2 | 3 | 2 | 3 | 2 | 2 | 3 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.6 | 0.94563 | 1.2474 | 0.49306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | distribution_location | TRUE | 3.0625 | 1 | 2 | 2 | 5 | 2 | 1 | 1 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 1.7554 | 2.3794 | 0.81944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | distribution_scale | TRUE | 3.25 | 2 | 2 | 1 | 3 | 1 | 2 | 3 | 2 | 1.75 | 1.75 | 1.75 | 2.0125 | 0.8588 | 1.1165 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | distribution_tail | TRUE | 3.2125 | 1 | 2 | 3 | 3 | 3 | 1 | 3 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 2.5625 | 1.2661 | 1.7629 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | distribution_mixture | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 3 | 2.5 | 2.125 | 2.125 | 2.125 | 2.3875 | 0.78632 | 0.96331 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | synchronous_switch | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.19834 | 0.20557 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | common_mode_drift | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.19834 | 0.20557 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | common_unequal | FALSE | 1.325 | 3 | 5 | 4 | 4 | 4 | 3 | 3 | 3.9 | 3.675 | 3.675 | 3.675 | 3.675 | 0.65621 | 0.76036 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-08 | 2026-03-02 12:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.6241 | 2.1003 | 0.90972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | baseline | FALSE | 2.55 | 3 | 3 | 2 | 2 | 2 | 3 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.1875 | 0.73438 | 0.84434 | 0.56944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | unilateral_drift | TRUE | 3.55 | 1 | 1 | 3 | 2 | 3 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 2.8618 | 4.1031 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | unilateral_step | TRUE | 3.325 | 1 | 3 | 2 | 2 | 2 | 1 | 1 | 1.9 | 1.675 | 1.675 | 1.675 | 1.675 | 1.5844 | 2.0435 | 0.89583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | unilateral_freeze | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.0756 | 2.8622 | 0.89583 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | unilateral_spike | TRUE | 2.8125 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2.25 | 2.1875 | 2.1875 | 2.1875 | 2.1875 | 0.93397 | 1.1724 | 0.57639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | distribution_location | TRUE | 3.325 | 1 | 3 | 2 | 2 | 2 | 1 | 1 | 1.9 | 1.675 | 1.675 | 1.675 | 1.675 | 2.4531 | 3.4219 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | distribution_scale | TRUE | 3.2125 | 2 | 3 | 1 | 2 | 1 | 3 | 2 | 2.05 | 1.7875 | 1.7875 | 2.05 | 1.7875 | 0.75651 | 0.89974 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | distribution_tail | TRUE | 3.1375 | 1 | 4 | 2 | 2 | 2 | 1 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.375 | 1.0931 | 1.4144 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | distribution_mixture | TRUE | 2.8375 | 2 | 5 | 1 | 2 | 1 | 2 | 2 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 0.8008 | 0.96892 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | synchronous_switch | FALSE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 5 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.6125 | 0.41573 | 0.48917 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | common_mode_drift | FALSE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 5 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.6125 | 0.41573 | 0.48917 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | common_unequal | FALSE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.5883 | 2.0824 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-09 | 2026-03-06 17:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 4 | 2 | 4 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 2.0435 | 2.7391 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | baseline | FALSE | 2.875 | 3 | 1 | 2 | 4 | 2 | 3 | 3 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 0.66949 | 0.81953 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | unilateral_drift | TRUE | 2.6875 | 1 | 4 | 3 | 4 | 3 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 2.6768 | 3.7992 | 0.99306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | unilateral_step | TRUE | 2.8375 | 1 | 4 | 2 | 4 | 2 | 1 | 1 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 1.4142 | 1.783 | 0.86111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | unilateral_freeze | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.937 | 2.6542 | 0.86111 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | unilateral_spike | TRUE | 3.1375 | 2 | 1 | 2 | 4 | 2 | 2 | 3 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.125 | 0.88147 | 1.1682 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | distribution_location | TRUE | 3.4 | 1 | 1 | 2 | 4 | 2 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 2.1626 | 2.9886 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | distribution_scale | TRUE | 3.2875 | 2 | 1 | 1 | 4 | 1 | 2 | 3 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.975 | 0.75259 | 0.94414 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | distribution_tail | TRUE | 3.4 | 1 | 1 | 2 | 4 | 2 | 1 | 3 | 1.8 | 1.6 | 1.6 | 1.6 | 2.125 | 1.0625 | 1.4375 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | distribution_mixture | TRUE | 2.4625 | 3 | 4 | 1 | 4 | 1 | 3 | 3 | 3.05 | 2.5375 | 2.5375 | 2.5375 | 2.5375 | 0.73229 | 0.90104 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | synchronous_switch | FALSE | 1.175 | 5 | 3 | 4 | 4 | 4 | 5 | 5 | 4.1 | 3.825 | 3.825 | 3.825 | 3.825 | 0.24767 | 0.2739 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | common_mode_drift | FALSE | 1.175 | 5 | 3 | 4 | 4 | 4 | 5 | 5 | 4.1 | 3.825 | 3.825 | 3.825 | 3.825 | 0.24767 | 0.2739 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | common_unequal | FALSE | 2.05 | 1 | 5 | 5 | 5 | 5 | 1 | 1 | 3.6 | 2.95 | 2.95 | 2.95 | 2.95 | 1.1506 | 1.4177 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-10 | 2026-03-10 22:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 4 | 5 | 4 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 2.0957 | 2.8262 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | baseline | FALSE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 4 | 3.5 | 3.125 | 3.125 | 3.125 | 3.3875 | 0.68619 | 0.86588 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | unilateral_drift | TRUE | 3.25 | 1 | 1 | 2 | 5 | 2 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.6618 | 2.2142 | 0.83333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | unilateral_step | TRUE | 3.3625 | 1 | 2 | 1 | 4 | 1 | 2 | 1 | 1.85 | 1.6375 | 1.6375 | 1.9 | 1.6375 | 1.0096 | 1.2151 | 0.70139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | unilateral_freeze | TRUE | 2.2 | 1 | 5 | 5 | 4 | 5 | 1 | 2 | 3.4 | 2.8 | 2.8 | 2.8 | 3.3125 | 1.4939 | 2.1056 | 0.57639 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | unilateral_spike | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 2 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.3875 | 0.85158 | 1.1276 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 2 | 5 | 2 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.9206 | 2.5715 | 0.94444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | distribution_scale | TRUE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 2 | 4 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.9875 | 0.7706 | 0.99729 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | distribution_tail | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 1 | 4 | 3.15 | 2.8625 | 2.8625 | 2.35 | 3.3875 | 0.94525 | 1.3115 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | distribution_mixture | TRUE | 2.275 | 3 | 5 | 1 | 4 | 1 | 3 | 3 | 3.3 | 2.725 | 2.725 | 2.725 | 2.725 | 0.70032 | 0.84776 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.20189 | 0.23925 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.20189 | 0.23925 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | common_unequal | FALSE | 2.725 | 1 | 3 | 4 | 4 | 4 | 2 | 1 | 2.7 | 2.275 | 2.275 | 2.7875 | 2.275 | 0.99927 | 1.2071 | 0.6875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-11 | 2026-03-15 03:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 5 | 4 | 5 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.466 | 1.8739 | 0.85417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | baseline | FALSE | 1.55 | 4 | 4 | 3 | 3 | 3 | 4 | 4 | 3.6 | 3.45 | 3.45 | 3.45 | 3.45 | 0.55238 | 0.67064 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | unilateral_drift | TRUE | 3.175 | 1 | 3 | 2 | 3 | 2 | 1 | 1 | 2.1 | 1.825 | 1.825 | 1.825 | 1.825 | 1.3132 | 1.6516 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | unilateral_step | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 1.8625 | 0.86453 | 1.0057 | 0.65278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | unilateral_freeze | TRUE | 1.8375 | 2 | 5 | 5 | 3 | 5 | 2 | 1 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 2.65 | 0.90674 | 1.0344 | 0.71528 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | unilateral_spike | TRUE | 2.1375 | 2 | 5 | 3 | 3 | 3 | 2 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.6375 | 0.76502 | 1.025 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | distribution_location | TRUE | 2.8375 | 1 | 4 | 3 | 3 | 3 | 1 | 1 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 1.9885 | 2.6984 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | distribution_scale | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 4 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.05 | 0.66946 | 0.83335 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | distribution_tail | TRUE | 2.1375 | 2 | 5 | 3 | 3 | 3 | 2 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.6375 | 0.91896 | 1.2585 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | distribution_mixture | TRUE | 2.6125 | 3 | 4 | 1 | 3 | 1 | 3 | 3 | 2.85 | 2.3875 | 2.3875 | 2.3875 | 2.3875 | 0.72176 | 0.88812 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.10996 | 0.095308 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.10996 | 0.095308 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | common_unequal | FALSE | 1.475 | 3 | 5 | 4 | 3 | 4 | 3 | 2 | 3.7 | 3.525 | 3.525 | 3.525 | 3.0125 | 0.71795 | 0.82621 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-12 | 2026-03-19 08:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.5106 | 1.9158 | 0.90278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | baseline | FALSE | 1.5125 | 3 | 4 | 3 | 5 | 3 | 3 | 2 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 2.975 | 0.68437 | 0.78414 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | unilateral_drift | TRUE | 3.2125 | 1 | 2 | 3 | 3 | 3 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 1.5225 | 2.0143 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | unilateral_step | TRUE | 3.3625 | 1 | 2 | 2 | 3 | 2 | 2 | 2 | 1.85 | 1.6375 | 1.6375 | 2.15 | 2.15 | 1.0063 | 1.2604 | 0.625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | unilateral_freeze | TRUE | 1.725 | 2 | 4 | 5 | 5 | 5 | 2 | 2 | 3.7 | 3.275 | 3.275 | 3.275 | 3.275 | 0.77551 | 0.9314 | 0.54167 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | unilateral_spike | TRUE | 2.025 | 2 | 4 | 3 | 5 | 3 | 2 | 2 | 3.3 | 2.975 | 2.975 | 2.975 | 2.975 | 0.91212 | 1.1637 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | distribution_location | TRUE | 2.8375 | 1 | 4 | 3 | 3 | 3 | 1 | 1 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 1.7956 | 2.3584 | 0.95139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | distribution_scale | TRUE | 2.175 | 2 | 4 | 2 | 5 | 2 | 3 | 3 | 3.1 | 2.825 | 2.825 | 3.0875 | 3.0875 | 0.74904 | 0.90118 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | distribution_tail | TRUE | 2.025 | 2 | 4 | 3 | 5 | 3 | 1 | 3 | 3.3 | 2.975 | 2.975 | 2.4625 | 3.4875 | 0.95404 | 1.2706 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | distribution_mixture | TRUE | 2.125 | 3 | 5 | 1 | 5 | 1 | 3 | 3 | 3.5 | 2.875 | 2.875 | 2.875 | 2.875 | 0.67833 | 0.81573 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.17705 | 0.20712 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.17705 | 0.20712 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | common_unequal | FALSE | 1.9875 | 2 | 5 | 4 | 3 | 4 | 2 | 3 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.525 | 0.79858 | 0.993 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-13 | 2026-03-23 14:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.7352 | 2.3132 | 0.86806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | baseline | FALSE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 3 | 3 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 2.7875 | 0.69697 | 0.83755 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | unilateral_drift | TRUE | 3.55 | 1 | 1 | 2 | 3 | 2 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.7428 | 2.3121 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | unilateral_step | TRUE | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.284 | 1.6262 | 0.77083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | unilateral_freeze | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.4637 | 1.9256 | 0.77083 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | unilateral_spike | TRUE | 2.475 | 2 | 4 | 2 | 3 | 2 | 2 | 3 | 2.7 | 2.525 | 2.525 | 2.525 | 2.7875 | 0.91135 | 1.1948 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | distribution_location | TRUE | 2.9875 | 1 | 4 | 2 | 3 | 2 | 1 | 1 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 2.0125 | 2.0534 | 2.7557 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | distribution_scale | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 3 | 2.5 | 2.125 | 2.125 | 2.125 | 2.3875 | 0.74336 | 0.9195 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | distribution_tail | TRUE | 2.475 | 2 | 4 | 2 | 3 | 2 | 1 | 4 | 2.7 | 2.525 | 2.525 | 2.0125 | 3.05 | 0.96694 | 1.3245 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | distribution_mixture | TRUE | 2.6875 | 2 | 5 | 1 | 3 | 1 | 2 | 2 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 0.77467 | 0.93463 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.1355 | 0.14713 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.1355 | 0.14713 | 0.11806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | common_unequal | FALSE | 1.9875 | 2 | 5 | 4 | 3 | 4 | 2 | 2 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.0125 | 0.79008 | 0.95105 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-14 | 2026-03-27 19:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.7133 | 2.2119 | 0.96528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | baseline | FALSE | 1.875 | 3 | 5 | 2 | 4 | 2 | 3 | 5 | 3.5 | 3.125 | 3.125 | 3.125 | 3.65 | 0.66518 | 0.87715 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | unilateral_drift | TRUE | 3.1 | 2 | 2 | 1 | 4 | 1 | 2 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.6375 | 0.97083 | 1.1273 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | unilateral_step | TRUE | 2.8375 | 3 | 2 | 1 | 4 | 1 | 3 | 2 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 1.9 | 0.72794 | 0.84287 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | unilateral_freeze | TRUE | 0.85 | 4 | 4 | 5 | 4 | 5 | 3 | 4 | 4.2 | 4.15 | 4.15 | 3.6375 | 4.15 | 0.56491 | 0.7054 | 0.35417 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | unilateral_spike | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 2 | 5 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.65 | 0.81345 | 1.1243 | 0.34722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | distribution_location | TRUE | 2.65 | 1 | 5 | 2 | 4 | 2 | 1 | 1 | 2.8 | 2.35 | 2.35 | 2.35 | 2.35 | 1.8818 | 2.5529 | 0.875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | distribution_scale | TRUE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 2 | 4 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.9875 | 0.77686 | 1.0448 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | distribution_tail | TRUE | 2.65 | 1 | 5 | 2 | 4 | 2 | 1 | 4 | 2.8 | 2.35 | 2.35 | 2.35 | 3.3875 | 1.0426 | 1.4738 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | distribution_mixture | TRUE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 2 | 3 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.725 | 0.75175 | 0.92884 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.22384 | 0.21103 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.22384 | 0.21103 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | common_unequal | FALSE | 1.4 | 4 | 4 | 3 | 4 | 3 | 4 | 3 | 3.8 | 3.6 | 3.6 | 3.6 | 3.3375 | 0.53932 | 0.58868 | 0.46528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-15 | 2026-04-01 | opposite_direction | FALSE | 3.1 | 1 | 1 | 4 | 4 | 4 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.2919 | 1.5375 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | baseline | FALSE | 1.35 | 5 | 5 | 2 | 4 | 2 | 4 | 5 | 4.2 | 3.65 | 3.65 | 3.3875 | 3.65 | 0.43631 | 0.52811 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | unilateral_drift | TRUE | 3.7 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3933 | 1.7758 | 0.81944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | unilateral_step | TRUE | 3.4 | 2 | 2 | 1 | 2 | 1 | 2 | 2 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 0.79737 | 0.97248 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | unilateral_freeze | TRUE | 1.6625 | 3 | 4 | 3 | 4 | 3 | 3 | 5 | 3.45 | 3.3375 | 3.3375 | 3.3375 | 3.8625 | 0.62386 | 0.81291 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | unilateral_spike | TRUE | 1.875 | 3 | 5 | 2 | 4 | 2 | 2 | 5 | 3.5 | 3.125 | 3.125 | 2.8625 | 3.65 | 0.67642 | 0.9144 | 0.31944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | distribution_location | TRUE | 2.65 | 1 | 5 | 2 | 4 | 2 | 1 | 1 | 2.8 | 2.35 | 2.35 | 2.35 | 2.35 | 1.6972 | 2.1945 | 0.95139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | distribution_scale | TRUE | 2.1625 | 4 | 5 | 1 | 3 | 1 | 4 | 4 | 3.45 | 2.8375 | 2.8375 | 2.8375 | 2.8375 | 0.54734 | 0.67613 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | distribution_tail | TRUE | 2.2875 | 2 | 5 | 2 | 3 | 2 | 2 | 5 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 3.5 | 0.74115 | 1.0501 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | distribution_mixture | TRUE | 2.6875 | 2 | 5 | 1 | 3 | 1 | 3 | 2 | 2.75 | 2.3125 | 2.3125 | 2.575 | 2.3125 | 0.74607 | 0.88697 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.25566 | 0.27795 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.25566 | 0.27795 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | common_unequal | FALSE | 2.25 | 3 | 3 | 4 | 2 | 4 | 3 | 4 | 3 | 2.75 | 2.75 | 2.75 | 3.0125 | 0.68573 | 0.86974 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-16 | 2026-04-05 05:00 | opposite_direction | FALSE | 3.4 | 1 | 1 | 5 | 1 | 5 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.4932 | 1.9239 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | baseline | FALSE | 0.4 | 5 | 5 | 4 | 5 | 4 | 4 | 5 | 4.8 | 4.6 | 4.6 | 4.3375 | 4.6 | 0.42741 | 0.56884 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | unilateral_drift | TRUE | 2.9125 | 1 | 2 | 3 | 5 | 3 | 1 | 1 | 2.45 | 2.0875 | 2.0875 | 2.0875 | 2.0875 | 1.0535 | 1.3067 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | unilateral_step | TRUE | 2.4 | 2 | 2 | 3 | 5 | 3 | 2 | 3 | 2.8 | 2.6 | 2.6 | 2.6 | 2.8625 | 0.82671 | 1.0306 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | unilateral_freeze | TRUE | 1.8375 | 2 | 5 | 3 | 5 | 3 | 2 | 5 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 4.2 | 0.82045 | 1.1637 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | unilateral_spike | TRUE | 1.175 | 3 | 5 | 4 | 5 | 4 | 3 | 5 | 4.1 | 3.825 | 3.825 | 3.825 | 4.6 | 0.5948 | 0.84318 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | distribution_location | TRUE | 2.2 | 1 | 5 | 4 | 5 | 4 | 1 | 1 | 3.4 | 2.8 | 2.8 | 2.8 | 2.8 | 1.5914 | 2.0967 | 0.83333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | distribution_scale | TRUE | 1.325 | 3 | 5 | 3 | 5 | 3 | 3 | 5 | 3.9 | 3.675 | 3.675 | 3.675 | 4.2 | 0.62056 | 0.83983 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | distribution_tail | TRUE | 1.175 | 3 | 5 | 4 | 5 | 4 | 2 | 5 | 4.1 | 3.825 | 3.825 | 3.3125 | 4.6 | 0.65433 | 0.91 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | distribution_mixture | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 3 | 4 | 3.7 | 3.275 | 3.275 | 3.275 | 3.5375 | 0.60901 | 0.72336 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.28622 | 0.33351 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.28622 | 0.33351 | 0.21528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | common_unequal | FALSE | 2.2125 | 2 | 3 | 3 | 5 | 3 | 2 | 3 | 3.05 | 2.7875 | 2.7875 | 2.7875 | 3.3 | 0.74479 | 0.90335 | 0.50694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-17 | 2026-04-09 10:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 4 | 5 | 4 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.4448 | 1.9172 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | baseline | FALSE | 0.4375 | 5 | 4 | 5 | 5 | 5 | 5 | 5 | 4.75 | 4.5625 | 4.5625 | 4.5625 | 4.5625 | 0.41366 | 0.49036 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | unilateral_drift | TRUE | 2.6875 | 2 | 1 | 4 | 5 | 4 | 2 | 2 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 0.89831 | 1.0944 | 0.60417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | unilateral_step | TRUE | 2.1375 | 3 | 2 | 3 | 5 | 3 | 3 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.125 | 0.59955 | 0.7261 | 0.40972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | unilateral_freeze | TRUE | 1.725 | 3 | 5 | 2 | 5 | 2 | 2 | 5 | 3.7 | 3.275 | 3.275 | 3.0125 | 3.8 | 0.69109 | 0.92496 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | unilateral_spike | TRUE | 0.7 | 4 | 4 | 5 | 5 | 5 | 3 | 5 | 4.4 | 4.3 | 4.3 | 3.7875 | 4.5625 | 0.55041 | 0.70902 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | distribution_location | TRUE | 2.2375 | 1 | 4 | 5 | 5 | 5 | 1 | 1 | 3.35 | 2.7625 | 2.7625 | 2.7625 | 2.7625 | 1.2979 | 1.6585 | 0.75694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | distribution_scale | TRUE | 1.7 | 3 | 3 | 3 | 5 | 3 | 3 | 4 | 3.4 | 3.3 | 3.3 | 3.3 | 3.5625 | 0.60518 | 0.77253 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | distribution_tail | TRUE | 0.85 | 4 | 4 | 4 | 5 | 4 | 3 | 5 | 4.2 | 4.15 | 4.15 | 3.6375 | 4.4125 | 0.52358 | 0.70134 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | distribution_mixture | TRUE | 1.0625 | 4 | 5 | 3 | 5 | 3 | 4 | 3 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.675 | 0.57175 | 0.64736 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | synchronous_switch | FALSE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.29507 | 0.36215 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | common_mode_drift | FALSE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.29507 | 0.36215 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | common_unequal | FALSE | 1.9875 | 3 | 2 | 4 | 5 | 4 | 3 | 4 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.275 | 0.60882 | 0.75082 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP12 | PAIR_ORP12-18 | 2026-04-13 16:00 | opposite_direction | FALSE | 2.8 | 1 | 1 | 5 | 5 | 5 | 1 | 1 | 2.6 | 2.2 | 2.2 | 2.2 | 2.2 | 1.2858 | 1.643 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | baseline | FALSE | 1.475 | 3 | 5 | 4 | 3 | 4 | 2 | 5 | 3.7 | 3.525 | 3.525 | 3.0125 | 4.05 | 0.70177 | 0.9937 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | unilateral_drift | TRUE | 1.4375 | 4 | 3 | 5 | 3 | 5 | 4 | 3 | 3.75 | 3.5625 | 3.5625 | 3.5625 | 3.3 | 0.5815 | 0.67288 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | unilateral_step | TRUE | 1.1375 | 5 | 4 | 4 | 3 | 4 | 5 | 5 | 4.15 | 3.8625 | 3.8625 | 3.8625 | 3.8625 | 0.37808 | 0.42643 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | unilateral_freeze | TRUE | 3.1375 | 1 | 4 | 1 | 3 | 1 | 1 | 3 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.3875 | 1.2832 | 1.796 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | unilateral_spike | TRUE | 1.475 | 3 | 5 | 4 | 3 | 4 | 2 | 5 | 3.7 | 3.525 | 3.525 | 3.0125 | 4.05 | 0.67785 | 0.97234 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | distribution_location | TRUE | 2.5 | 1 | 5 | 4 | 3 | 4 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.392 | 1.8293 | 0.73611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | distribution_scale | TRUE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 3 | 5 | 4.25 | 3.9375 | 3.9375 | 3.675 | 4.2 | 0.58057 | 0.80559 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | distribution_tail | TRUE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.32467 | 0.43 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | distribution_mixture | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 4 | 3 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 3.375 | 0.53879 | 0.57853 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.34845 | 0.40483 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.34845 | 0.40483 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | common_unequal | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.36375 | 0.4257 | 0.27083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-01 | 2026-02-01 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 2 | 1 | 2.2 | 1.9 | 1.9 | 2.1625 | 1.9 | 1.0381 | 1.2579 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | baseline | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.19821 | 0.20535 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | unilateral_drift | TRUE | 3.0625 | 1 | 2 | 5 | 2 | 5 | 1 | 1 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 1.0324 | 1.2716 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | unilateral_step | TRUE | 2.2875 | 3 | 2 | 5 | 2 | 5 | 3 | 3 | 2.95 | 2.7125 | 2.7125 | 2.7125 | 2.7125 | 0.62728 | 0.73991 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | unilateral_freeze | TRUE | 2.55 | 3 | 3 | 2 | 2 | 2 | 3 | 4 | 2.6 | 2.45 | 2.45 | 2.45 | 2.7125 | 0.64919 | 0.79494 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | unilateral_spike | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.29565 | 0.38628 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 5 | 2 | 5 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.2347 | 1.5579 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | distribution_scale | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.21981 | 0.24136 | 0.1875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | distribution_tail | TRUE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.29322 | 0.41925 | 0.10417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | distribution_mixture | TRUE | 1.1 | 5 | 5 | 3 | 3 | 3 | 5 | 4 | 4.2 | 3.9 | 3.9 | 3.9 | 3.6375 | 0.43208 | 0.48403 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.2175 | 0.20046 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.2175 | 0.20046 | 0.24306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | common_unequal | FALSE | 2.1 | 3 | 3 | 5 | 2 | 5 | 3 | 2 | 3.2 | 2.9 | 2.9 | 2.9 | 2.6375 | 0.7235 | 0.83546 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-02 | 2026-02-05 05:00 | opposite_direction | FALSE | 3.55 | 1 | 1 | 3 | 2 | 3 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 1.2349 | 1.5118 | 0.81944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | baseline | FALSE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 5 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.6125 | 0.18167 | 0.21483 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | unilateral_drift | TRUE | 2.6875 | 1 | 4 | 5 | 2 | 5 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 1.1222 | 1.4306 | 0.65972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | unilateral_step | TRUE | 2.325 | 2 | 4 | 4 | 2 | 4 | 2 | 2 | 2.9 | 2.675 | 2.675 | 2.675 | 2.675 | 0.83423 | 0.98297 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | unilateral_freeze | TRUE | 3.4375 | 2 | 1 | 2 | 2 | 2 | 2 | 3 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.825 | 0.74182 | 0.92155 | 0.47222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | unilateral_spike | TRUE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 5 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.6125 | 0.29675 | 0.39737 | 0.14583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | distribution_location | TRUE | 2.6875 | 1 | 4 | 5 | 2 | 5 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 1.4361 | 1.8426 | 0.82639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | distribution_scale | TRUE | 1.5375 | 5 | 4 | 4 | 2 | 4 | 5 | 5 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.32851 | 0.34844 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | distribution_tail | TRUE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 4 | 5 | 4.15 | 3.6125 | 3.6125 | 3.35 | 3.6125 | 0.44069 | 0.60022 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | distribution_mixture | TRUE | 1.9125 | 4 | 5 | 2 | 2 | 2 | 4 | 4 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.47585 | 0.52456 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | synchronous_switch | FALSE | 1.7875 | 5 | 4 | 5 | 1 | 5 | 5 | 5 | 3.95 | 3.2125 | 3.2125 | 3.2125 | 3.2125 | 0.20553 | 0.22682 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | common_mode_drift | FALSE | 1.7875 | 5 | 4 | 5 | 1 | 5 | 5 | 5 | 3.95 | 3.2125 | 3.2125 | 3.2125 | 3.2125 | 0.20553 | 0.22682 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | common_unequal | FALSE | 2.1375 | 2 | 5 | 4 | 2 | 4 | 2 | 3 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.125 | 0.78071 | 0.98173 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-03 | 2026-02-09 10:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.9696 | 2.704 | 0.86806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | baseline | FALSE | 2.7 | 2 | 2 | 3 | 3 | 3 | 2 | 4 | 2.4 | 2.3 | 2.3 | 2.3 | 2.825 | 0.75923 | 0.97371 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | unilateral_drift | TRUE | 2.8375 | 1 | 4 | 3 | 3 | 3 | 1 | 1 | 2.55 | 2.1625 | 2.1625 | 2.1625 | 2.1625 | 1.0769 | 1.3411 | 0.68056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | unilateral_step | TRUE | 2.6625 | 2 | 3 | 2 | 3 | 2 | 2 | 2 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.3375 | 0.82643 | 1.0024 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | unilateral_freeze | TRUE | 1.5125 | 3 | 4 | 5 | 3 | 5 | 3 | 2 | 3.65 | 3.4875 | 3.4875 | 3.4875 | 2.975 | 0.70124 | 0.78447 | 0.57639 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | unilateral_spike | TRUE | 2.5125 | 2 | 3 | 3 | 3 | 3 | 2 | 4 | 2.65 | 2.4875 | 2.4875 | 2.4875 | 3.2625 | 0.91968 | 1.2411 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | distribution_location | TRUE | 3.2125 | 1 | 2 | 3 | 3 | 3 | 1 | 1 | 2.05 | 1.7875 | 1.7875 | 1.7875 | 1.7875 | 1.5548 | 2.0311 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | distribution_scale | TRUE | 2.85 | 2 | 2 | 2 | 3 | 2 | 2 | 3 | 2.2 | 2.15 | 2.15 | 2.15 | 2.4125 | 0.81433 | 1.0609 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | distribution_tail | TRUE | 2.5125 | 2 | 3 | 3 | 3 | 3 | 2 | 4 | 2.65 | 2.4875 | 2.4875 | 2.4875 | 3.2625 | 0.7722 | 1.0463 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | distribution_mixture | TRUE | 2.425 | 3 | 5 | 1 | 3 | 1 | 3 | 3 | 3.1 | 2.575 | 2.575 | 2.575 | 2.575 | 0.69311 | 0.85426 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | synchronous_switch | FALSE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 5 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.6125 | 0.26428 | 0.2414 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | common_mode_drift | FALSE | 1.3875 | 5 | 4 | 5 | 2 | 5 | 5 | 5 | 4.15 | 3.6125 | 3.6125 | 3.6125 | 3.6125 | 0.26428 | 0.2414 | 0.29861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | common_unequal | FALSE | 1.2125 | 4 | 5 | 4 | 3 | 4 | 5 | 3 | 4.05 | 3.7875 | 3.7875 | 4.05 | 3.525 | 0.48558 | 0.51301 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-04 | 2026-02-13 15:00 | opposite_direction | FALSE | 3.0625 | 1 | 2 | 5 | 2 | 5 | 1 | 1 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 1.5531 | 1.9774 | 0.91667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | baseline | FALSE | 2.55 | 2 | 2 | 3 | 4 | 3 | 3 | 2 | 2.6 | 2.45 | 2.45 | 2.7125 | 2.45 | 0.7405 | 0.87305 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | unilateral_drift | TRUE | 3.4 | 1 | 1 | 2 | 4 | 2 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.3173 | 1.663 | 0.79861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | unilateral_step | TRUE | 3.1 | 2 | 2 | 1 | 4 | 1 | 2 | 2 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 0.85977 | 1.0163 | 0.625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | unilateral_freeze | TRUE | 1.9875 | 2 | 5 | 3 | 4 | 3 | 2 | 4 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.7875 | 0.76632 | 0.99017 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | unilateral_spike | TRUE | 2.55 | 2 | 2 | 3 | 4 | 3 | 2 | 3 | 2.6 | 2.45 | 2.45 | 2.45 | 2.7125 | 0.83209 | 1.0442 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | distribution_location | TRUE | 3.0625 | 1 | 2 | 3 | 4 | 3 | 1 | 1 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 2.2847 | 3.1412 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | distribution_scale | TRUE | 2.875 | 3 | 1 | 2 | 4 | 2 | 3 | 3 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 0.73037 | 0.87006 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | distribution_tail | TRUE | 3.0625 | 1 | 2 | 3 | 4 | 3 | 1 | 2 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 2.45 | 1.0085 | 1.3013 | 0.56944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | distribution_mixture | TRUE | 2.5375 | 2 | 5 | 1 | 4 | 1 | 3 | 2 | 2.95 | 2.4625 | 2.4625 | 2.725 | 2.4625 | 0.73675 | 0.85291 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | synchronous_switch | FALSE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.38749 | 0.45137 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | common_mode_drift | FALSE | 0.5875 | 5 | 4 | 4 | 5 | 4 | 5 | 5 | 4.55 | 4.4125 | 4.4125 | 4.4125 | 4.4125 | 0.38749 | 0.45137 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | common_unequal | FALSE | 2.55 | 2 | 2 | 3 | 4 | 3 | 2 | 2 | 2.6 | 2.45 | 2.45 | 2.45 | 2.45 | 0.93477 | 1.1274 | 0.64583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-05 | 2026-02-17 20:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 5 | 4 | 5 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.4806 | 1.8705 | 0.89583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | baseline | FALSE | 1.2125 | 4 | 5 | 4 | 3 | 4 | 4 | 4 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.7875 | 0.54153 | 0.6618 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | unilateral_drift | TRUE | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0.69555 | 0.8074 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | unilateral_step | TRUE | 2.2125 | 3 | 4 | 2 | 3 | 2 | 4 | 3 | 3.05 | 2.7875 | 2.7875 | 3.05 | 2.7875 | 0.5982 | 0.66367 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | unilateral_freeze | TRUE | 3.3625 | 1 | 2 | 3 | 2 | 3 | 1 | 1 | 1.85 | 1.6375 | 1.6375 | 1.6375 | 1.6375 | 2.1951 | 3.1584 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | unilateral_spike | TRUE | 1.475 | 3 | 5 | 4 | 3 | 4 | 2 | 4 | 3.7 | 3.525 | 3.525 | 3.0125 | 3.7875 | 0.70247 | 0.92542 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | distribution_location | TRUE | 2.65 | 1 | 5 | 4 | 2 | 4 | 1 | 1 | 2.8 | 2.35 | 2.35 | 2.35 | 2.35 | 1.1709 | 1.4422 | 0.76389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | distribution_scale | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 4 | 4 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 3.6375 | 0.56737 | 0.66784 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | distribution_tail | TRUE | 1.475 | 3 | 5 | 4 | 3 | 4 | 2 | 5 | 3.7 | 3.525 | 3.525 | 3.0125 | 4.05 | 0.71103 | 0.97672 | 0.3125 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | distribution_mixture | TRUE | 2.425 | 3 | 5 | 1 | 3 | 1 | 4 | 3 | 3.1 | 2.575 | 2.575 | 2.8375 | 2.575 | 0.61652 | 0.69419 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.2642 | 0.26905 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.2642 | 0.26905 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | common_unequal | FALSE | 1.75 | 5 | 5 | 4 | 1 | 4 | 5 | 4 | 4 | 3.25 | 3.25 | 3.25 | 2.9875 | 0.34755 | 0.31999 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-06 | 2026-02-22 01:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.4006 | 1.7973 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | baseline | FALSE | 0.85 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 4.2 | 4.15 | 4.15 | 4.15 | 4.15 | 0.51155 | 0.58406 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | unilateral_drift | TRUE | 2.3625 | 2 | 3 | 4 | 3 | 4 | 2 | 2 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.6375 | 0.94087 | 1.1376 | 0.64583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | unilateral_step | TRUE | 2.25 | 3 | 3 | 4 | 2 | 4 | 3 | 4 | 3 | 2.75 | 2.75 | 2.75 | 3.0125 | 0.62967 | 0.76705 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | unilateral_freeze | TRUE | 1.95 | 4 | 4 | 2 | 3 | 2 | 4 | 5 | 3.4 | 3.05 | 3.05 | 3.05 | 3.3125 | 0.47557 | 0.59817 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | unilateral_spike | TRUE | 1.3625 | 3 | 4 | 4 | 5 | 4 | 3 | 4 | 3.85 | 3.6375 | 3.6375 | 3.6375 | 4.15 | 0.66349 | 0.84193 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | distribution_location | TRUE | 2.6875 | 1 | 4 | 4 | 3 | 4 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 1.1246 | 1.4067 | 0.70139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | distribution_scale | TRUE | 1.25 | 4 | 4 | 3 | 5 | 3 | 4 | 4 | 4 | 3.75 | 3.75 | 3.75 | 3.75 | 0.56369 | 0.65708 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | distribution_tail | TRUE | 1.175 | 3 | 5 | 4 | 5 | 4 | 3 | 4 | 4.1 | 3.825 | 3.825 | 3.825 | 4.3375 | 0.649 | 0.8363 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | distribution_mixture | TRUE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 3 | 3 | 3.45 | 3.0875 | 3.0875 | 3.0875 | 3.0875 | 0.63744 | 0.71981 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.3364 | 0.3477 | 0.31944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.3364 | 0.3477 | 0.31944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | common_unequal | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.4016 | 0.45174 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-07 | 2026-02-26 07:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.5475 | 2.0143 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | baseline | FALSE | 1.475 | 3 | 5 | 3 | 4 | 3 | 3 | 4 | 3.7 | 3.525 | 3.525 | 3.525 | 3.7875 | 0.64402 | 0.83725 | 0.35417 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | unilateral_drift | TRUE | 3.4 | 1 | 1 | 2 | 4 | 2 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.4204 | 1.8211 | 0.81944 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | unilateral_step | TRUE | 3.1 | 2 | 2 | 1 | 4 | 1 | 2 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.6375 | 0.92429 | 1.1053 | 0.65278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | unilateral_freeze | TRUE | 2.025 | 2 | 4 | 4 | 4 | 4 | 1 | 5 | 3.3 | 2.975 | 2.975 | 2.4625 | 4.2625 | 0.90707 | 1.3359 | 0.26389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | unilateral_spike | TRUE | 1.9875 | 2 | 5 | 3 | 4 | 3 | 2 | 4 | 3.35 | 3.0125 | 3.0125 | 3.0125 | 3.7875 | 0.81758 | 1.1173 | 0.36806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | distribution_location | TRUE | 2.35 | 1 | 5 | 3 | 5 | 3 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.883 | 2.5225 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | distribution_scale | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 2 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.3875 | 0.78386 | 1.0287 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | distribution_tail | TRUE | 2.1375 | 2 | 5 | 2 | 4 | 2 | 2 | 4 | 3.15 | 2.8625 | 2.8625 | 2.8625 | 3.3875 | 0.90832 | 1.2361 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | distribution_mixture | TRUE | 2.275 | 3 | 5 | 1 | 4 | 1 | 3 | 3 | 3.3 | 2.725 | 2.725 | 2.725 | 2.725 | 0.68758 | 0.82652 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | synchronous_switch | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.23316 | 0.28212 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | common_mode_drift | FALSE | 0.4 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 4.8 | 4.6 | 4.6 | 4.6 | 4.6 | 0.23316 | 0.28212 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | common_unequal | FALSE | 2.875 | 1 | 3 | 3 | 4 | 3 | 2 | 2 | 2.5 | 2.125 | 2.125 | 2.6375 | 2.6375 | 0.98338 | 1.2316 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-08 | 2026-03-02 12:00 | opposite_direction | FALSE | 2.95 | 1 | 1 | 5 | 4 | 5 | 1 | 1 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 1.4238 | 1.7943 | 0.86806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | baseline | FALSE | 3.325 | 1 | 3 | 1 | 3 | 1 | 1 | 1 | 1.9 | 1.675 | 1.675 | 1.675 | 1.675 | 1.0742 | 1.2903 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | unilateral_drift | TRUE | 3.475 | 1 | 3 | 1 | 2 | 1 | 1 | 1 | 1.7 | 1.525 | 1.525 | 1.525 | 1.525 | 2.3118 | 3.1864 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | unilateral_step | TRUE | 3.2875 | 1 | 4 | 1 | 2 | 1 | 1 | 1 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.7125 | 1.3456 | 1.6084 | 0.95139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | unilateral_freeze | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 3.0749 | 4.4905 | 0.95139 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | unilateral_spike | TRUE | 3.325 | 1 | 3 | 1 | 3 | 1 | 1 | 1 | 1.9 | 1.675 | 1.675 | 1.675 | 1.675 | 1.2991 | 1.6651 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | distribution_location | TRUE | 3.025 | 1 | 3 | 1 | 5 | 1 | 1 | 1 | 2.3 | 1.975 | 1.975 | 1.975 | 1.975 | 2.7091 | 3.8485 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | distribution_scale | TRUE | 3.0625 | 2 | 3 | 1 | 3 | 1 | 2 | 1 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.675 | 0.92567 | 1.103 | 0.65972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | distribution_tail | TRUE | 3.325 | 1 | 3 | 1 | 3 | 1 | 1 | 1 | 1.9 | 1.675 | 1.675 | 1.675 | 1.675 | 1.4455 | 1.8721 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | distribution_mixture | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 3 | 2.5 | 2.125 | 2.125 | 2.125 | 2.3875 | 0.75565 | 0.93534 | 0.48611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.43208 | 0.49329 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.43208 | 0.49329 | 0.34028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | common_unequal | FALSE | 2.8 | 1 | 5 | 4 | 1 | 4 | 1 | 1 | 2.6 | 2.2 | 2.2 | 2.2 | 2.2 | 1.3147 | 1.6031 | 0.88194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-09 | 2026-03-06 17:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 2.0552 | 2.7586 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | baseline | FALSE | 1.9125 | 3 | 4 | 2 | 5 | 2 | 2 | 4 | 3.45 | 3.0875 | 3.0875 | 2.825 | 3.35 | 0.72487 | 0.92108 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | unilateral_drift | TRUE | 3.4 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.4796 | 1.8873 | 0.86806 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | unilateral_step | TRUE | 3.4 | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.0729 | 1.3159 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | unilateral_freeze | TRUE | 1.5375 | 2 | 5 | 5 | 5 | 5 | 2 | 2 | 3.95 | 3.4625 | 3.4625 | 3.4625 | 3.4625 | 0.91705 | 1.1534 | 0.5625 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | unilateral_spike | TRUE | 1.9875 | 2 | 5 | 2 | 5 | 2 | 1 | 4 | 3.35 | 3.0125 | 3.0125 | 2.5 | 3.5375 | 0.94195 | 1.2782 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | distribution_location | TRUE | 2.6875 | 1 | 4 | 2 | 5 | 2 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 1.9097 | 2.5347 | 0.97222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | distribution_scale | TRUE | 2.575 | 2 | 4 | 1 | 5 | 1 | 2 | 3 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.79039 | 1.0118 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | distribution_tail | TRUE | 2.5 | 1 | 5 | 2 | 5 | 2 | 1 | 3 | 3 | 2.5 | 2.5 | 2.5 | 3.275 | 1.0469 | 1.4486 | 0.44444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | distribution_mixture | TRUE | 2.3875 | 2 | 5 | 1 | 5 | 1 | 2 | 3 | 3.15 | 2.6125 | 2.6125 | 2.6125 | 2.875 | 0.78451 | 0.95566 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | synchronous_switch | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.24571 | 0.27526 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | common_mode_drift | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0.24571 | 0.27526 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | common_unequal | FALSE | 2.4 | 2 | 2 | 3 | 5 | 3 | 2 | 3 | 2.8 | 2.6 | 2.6 | 2.6 | 2.8625 | 0.75099 | 0.91832 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-10 | 2026-03-10 22:00 | opposite_direction | FALSE | 2.8 | 1 | 1 | 5 | 5 | 5 | 1 | 1 | 2.6 | 2.2 | 2.2 | 2.2 | 2.2 | 1.5072 | 1.9195 | 0.88889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | baseline | FALSE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 3 | 2 | 2.45 | 2.3375 | 2.3375 | 2.6 | 2.3375 | 0.73985 | 0.87198 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | unilateral_drift | TRUE | 3.4375 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1.75 | 1.5625 | 1.5625 | 1.5625 | 1.3 | 0.894 | 1.0363 | 0.68056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | unilateral_step | TRUE | 3.4 | 2 | 2 | 1 | 2 | 1 | 3 | 2 | 1.8 | 1.6 | 1.6 | 1.8625 | 1.6 | 0.75257 | 0.8978 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | unilateral_freeze | TRUE | 2.6875 | 1 | 4 | 5 | 2 | 5 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 1.8608 | 2.5365 | 0.84722 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | unilateral_spike | TRUE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 2 | 2 | 2.45 | 2.3375 | 2.3375 | 2.3375 | 2.3375 | 0.88403 | 1.1123 | 0.54167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | distribution_location | TRUE | 2.875 | 1 | 3 | 3 | 4 | 3 | 1 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 1.4981 | 1.9366 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | distribution_scale | TRUE | 2.8125 | 2 | 3 | 2 | 2 | 2 | 2 | 3 | 2.25 | 2.1875 | 2.1875 | 2.1875 | 2.45 | 0.81729 | 1.0103 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | distribution_tail | TRUE | 2.6625 | 2 | 3 | 3 | 2 | 3 | 1 | 3 | 2.45 | 2.3375 | 2.3375 | 1.825 | 2.6 | 0.96725 | 1.2926 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | distribution_mixture | TRUE | 3.025 | 2 | 4 | 1 | 2 | 1 | 3 | 2 | 2.3 | 1.975 | 1.975 | 2.2375 | 1.975 | 0.73991 | 0.8767 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | synchronous_switch | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.33304 | 0.36525 | 0.28472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | common_mode_drift | FALSE | 1.35 | 5 | 5 | 4 | 2 | 4 | 5 | 5 | 4.2 | 3.65 | 3.65 | 3.65 | 3.65 | 0.33304 | 0.36525 | 0.28472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | common_unequal | FALSE | 2.95 | 3 | 3 | 1 | 2 | 1 | 3 | 3 | 2.4 | 2.05 | 2.05 | 2.05 | 2.05 | 0.7123 | 0.83995 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-11 | 2026-03-15 03:00 | opposite_direction | FALSE | 2.9875 | 2 | 1 | 5 | 2 | 5 | 2 | 1 | 2.35 | 2.0125 | 2.0125 | 2.0125 | 1.75 | 0.95262 | 1.1155 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | baseline | FALSE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 2 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 0.86001 | 1.0676 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | unilateral_drift | TRUE | 3.7 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1.4 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3357 | 1.6659 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | unilateral_step | TRUE | 3.0625 | 2 | 3 | 1 | 3 | 1 | 2 | 2 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 0.82645 | 0.97 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | unilateral_freeze | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 3.5252 | 5.3013 | 0.86111 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | unilateral_spike | TRUE | 3.1375 | 1 | 4 | 1 | 3 | 1 | 1 | 2 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 2.125 | 1.0779 | 1.4215 | 0.5625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | distribution_location | TRUE | 3.1375 | 1 | 4 | 1 | 3 | 1 | 1 | 1 | 2.15 | 1.8625 | 1.8625 | 1.8625 | 1.8625 | 2.0635 | 2.7725 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | distribution_scale | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 2 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 0.85599 | 1.0702 | 0.53472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | distribution_tail | TRUE | 2.95 | 1 | 5 | 1 | 3 | 1 | 1 | 3 | 2.4 | 2.05 | 2.05 | 2.05 | 2.575 | 1.077 | 1.4617 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | distribution_mixture | TRUE | 2.6875 | 2 | 5 | 1 | 3 | 1 | 2 | 3 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.575 | 0.82055 | 1.025 | 0.51389 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.19944 | 0.22592 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.19944 | 0.22592 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | common_unequal | FALSE | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0.72176 | 0.85108 | 0.52778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-12 | 2026-03-19 08:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.3403 | 1.6736 | 0.84028 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | baseline | FALSE | 3.0625 | 2 | 3 | 1 | 3 | 1 | 2 | 3 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 2.2 | 0.824 | 1.0678 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | unilateral_drift | TRUE | 3.55 | 1 | 1 | 2 | 3 | 2 | 1 | 1 | 1.6 | 1.45 | 1.45 | 1.45 | 1.45 | 2.1265 | 2.933 | 0.91667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | unilateral_step | TRUE | 3.325 | 1 | 3 | 1 | 3 | 1 | 1 | 1 | 1.9 | 1.675 | 1.675 | 1.675 | 1.675 | 1.2719 | 1.5827 | 0.80556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | unilateral_freeze | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 2.4065 | 3.4738 | 0.80556 | 1 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | unilateral_spike | TRUE | 3.325 | 1 | 3 | 1 | 3 | 1 | 1 | 4 | 1.9 | 1.675 | 1.675 | 1.675 | 2.4625 | 1.0486 | 1.456 | 0.4375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | distribution_location | TRUE | 3.325 | 1 | 3 | 1 | 3 | 1 | 1 | 1 | 1.9 | 1.675 | 1.675 | 1.675 | 1.675 | 2.1293 | 2.8822 | 1 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | distribution_scale | TRUE | 3.0625 | 2 | 3 | 1 | 3 | 1 | 2 | 3 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 2.2 | 0.87569 | 1.14 | 0.47917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | distribution_tail | TRUE | 3.325 | 1 | 3 | 1 | 3 | 1 | 1 | 3 | 1.9 | 1.675 | 1.675 | 1.675 | 2.2 | 1.0046 | 1.3687 | 0.45833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | distribution_mixture | TRUE | 2.875 | 2 | 4 | 1 | 3 | 1 | 2 | 2 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 0.79178 | 0.9539 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | synchronous_switch | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.17709 | 0.18867 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | common_mode_drift | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.17709 | 0.18867 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | common_unequal | FALSE | 1.8375 | 2 | 5 | 5 | 3 | 5 | 2 | 2 | 3.55 | 3.1625 | 3.1625 | 3.1625 | 3.1625 | 0.94758 | 1.1626 | 0.625 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-13 | 2026-03-23 14:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9676 | 2.6636 | 0.92361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | baseline | FALSE | 2.875 | 1 | 3 | 3 | 4 | 3 | 1 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 1.2065 | 1.5108 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | unilateral_drift | TRUE | 3.6625 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1.45 | 1.3375 | 1.3375 | 1.3375 | 1.3375 | 1.2976 | 1.6395 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | unilateral_step | TRUE | 3.85 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1.2 | 1.15 | 1.15 | 1.15 | 1.15 | 1.087 | 1.3117 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | unilateral_freeze | TRUE | 2.35 | 1 | 5 | 4 | 4 | 4 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 2.1726 | 3.1211 | 0.75 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | unilateral_spike | TRUE | 2.875 | 1 | 3 | 3 | 4 | 3 | 1 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 1.2674 | 1.6169 | 0.74306 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | distribution_location | TRUE | 3.175 | 1 | 3 | 3 | 2 | 3 | 1 | 1 | 2.1 | 1.825 | 1.825 | 1.825 | 1.825 | 2.3411 | 3.2954 | 0.90972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | distribution_scale | TRUE | 3.025 | 1 | 3 | 2 | 4 | 2 | 1 | 1 | 2.3 | 1.975 | 1.975 | 1.975 | 1.975 | 1.0931 | 1.3727 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | distribution_tail | TRUE | 2.875 | 1 | 3 | 3 | 4 | 3 | 1 | 1 | 2.5 | 2.125 | 2.125 | 2.125 | 2.125 | 1.6179 | 2.1734 | 0.78472 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | distribution_mixture | TRUE | 2.575 | 3 | 5 | 1 | 2 | 1 | 3 | 4 | 2.9 | 2.425 | 2.425 | 2.425 | 2.6875 | 0.6411 | 0.78609 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | synchronous_switch | FALSE | 1.875 | 3 | 5 | 4 | 2 | 4 | 4 | 2 | 3.5 | 3.125 | 3.125 | 3.3875 | 2.8625 | 0.60243 | 0.60591 | 0.59722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | common_mode_drift | FALSE | 1.875 | 3 | 5 | 4 | 2 | 4 | 4 | 2 | 3.5 | 3.125 | 3.125 | 3.3875 | 2.8625 | 0.60243 | 0.60591 | 0.59722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | common_unequal | FALSE | 3.325 | 1 | 3 | 2 | 2 | 2 | 2 | 1 | 1.9 | 1.675 | 1.675 | 2.1875 | 1.675 | 1.0332 | 1.2498 | 0.70833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-14 | 2026-03-27 19:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.3271 | 1.6702 | 0.8125 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | baseline | FALSE | 1.1375 | 5 | 4 | 4 | 3 | 4 | 4 | 5 | 4.15 | 3.8625 | 3.8625 | 3.6 | 3.8625 | 0.43795 | 0.57251 | 0.23611 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | unilateral_drift | TRUE | 2.175 | 2 | 4 | 4 | 3 | 4 | 2 | 2 | 3.1 | 2.825 | 2.825 | 2.825 | 2.825 | 0.94789 | 1.1724 | 0.61111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | unilateral_step | TRUE | 1.55 | 4 | 4 | 3 | 3 | 3 | 4 | 4 | 3.6 | 3.45 | 3.45 | 3.45 | 3.45 | 0.55239 | 0.63824 | 0.42361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | unilateral_freeze | TRUE | 3.2875 | 2 | 1 | 2 | 3 | 2 | 2 | 3 | 1.95 | 1.7125 | 1.7125 | 1.7125 | 1.975 | 0.88582 | 1.1754 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | unilateral_spike | TRUE | 1.4 | 4 | 4 | 4 | 3 | 4 | 3 | 5 | 3.8 | 3.6 | 3.6 | 3.3375 | 3.8625 | 0.54467 | 0.74112 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | distribution_location | TRUE | 2.6875 | 1 | 4 | 4 | 3 | 4 | 1 | 1 | 2.75 | 2.3125 | 2.3125 | 2.3125 | 2.3125 | 1.2488 | 1.623 | 0.6875 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | distribution_scale | TRUE | 1.3625 | 4 | 5 | 3 | 3 | 3 | 3 | 5 | 3.85 | 3.6375 | 3.6375 | 3.375 | 3.9 | 0.55376 | 0.70071 | 0.33333 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | distribution_tail | TRUE | 1.4 | 4 | 4 | 4 | 3 | 4 | 4 | 5 | 3.8 | 3.6 | 3.6 | 3.6 | 3.8625 | 0.51699 | 0.67647 | 0.27778 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | distribution_mixture | TRUE | 1.95 | 4 | 4 | 2 | 3 | 2 | 4 | 4 | 3.4 | 3.05 | 3.05 | 3.05 | 3.05 | 0.53173 | 0.63159 | 0.38194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | synchronous_switch | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.18836 | 0.23985 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | common_mode_drift | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.18836 | 0.23985 | 0.11111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | common_unequal | FALSE | 1.0625 | 4 | 5 | 5 | 3 | 5 | 4 | 4 | 4.25 | 3.9375 | 3.9375 | 3.9375 | 3.9375 | 0.49198 | 0.55146 | 0.40278 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-15 | 2026-04-01 | opposite_direction | FALSE | 3.25 | 1 | 1 | 4 | 3 | 4 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.6721 | 2.1896 | 0.89583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | baseline | FALSE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 4 | 4.4 | 4.05 | 4.05 | 4.05 | 3.7875 | 0.35312 | 0.33854 | 0.375 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | unilateral_drift | TRUE | 2.3625 | 2 | 3 | 5 | 2 | 5 | 2 | 1 | 2.85 | 2.6375 | 2.6375 | 2.6375 | 2.125 | 0.93411 | 1.0939 | 0.69444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | unilateral_step | TRUE | 2.25 | 3 | 3 | 4 | 2 | 4 | 3 | 3 | 3 | 2.75 | 2.75 | 2.75 | 2.75 | 0.64938 | 0.74896 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | unilateral_freeze | TRUE | 2.425 | 3 | 5 | 1 | 3 | 1 | 3 | 4 | 3.1 | 2.575 | 2.575 | 2.575 | 2.8375 | 0.67778 | 0.84259 | 0.43056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | unilateral_spike | TRUE | 1.2125 | 4 | 5 | 4 | 3 | 4 | 4 | 4 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.7875 | 0.47519 | 0.55124 | 0.36111 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | distribution_location | TRUE | 2.5 | 1 | 5 | 4 | 3 | 4 | 1 | 1 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 1.5807 | 1.991 | 0.96528 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | distribution_scale | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.14937 | 0.13321 | 0.17361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | distribution_tail | TRUE | 1.475 | 3 | 5 | 4 | 3 | 4 | 3 | 4 | 3.7 | 3.525 | 3.525 | 3.525 | 3.7875 | 0.58491 | 0.71097 | 0.39583 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | distribution_mixture | TRUE | 1.2125 | 4 | 5 | 3 | 4 | 3 | 4 | 3 | 4.05 | 3.7875 | 3.7875 | 3.7875 | 3.525 | 0.52139 | 0.52176 | 0.52083 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | synchronous_switch | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.23197 | 0.21532 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | common_mode_drift | FALSE | 1.2 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 4.4 | 3.8 | 3.8 | 3.8 | 3.8 | 0.23197 | 0.21532 | 0.25694 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | common_unequal | FALSE | 1.65 | 4 | 4 | 5 | 2 | 5 | 4 | 3 | 3.8 | 3.35 | 3.35 | 3.35 | 3.0875 | 0.56779 | 0.64538 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-16 | 2026-04-05 05:00 | opposite_direction | FALSE | 3.25 | 1 | 1 | 5 | 2 | 5 | 1 | 1 | 2 | 1.75 | 1.75 | 1.75 | 1.75 | 1.4228 | 1.7509 | 0.93056 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | baseline | FALSE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.18782 | 0.17877 | 0.20139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | unilateral_drift | TRUE | 2.6125 | 3 | 4 | 3 | 1 | 3 | 3 | 2 | 2.85 | 2.3875 | 2.3875 | 2.3875 | 2.125 | 0.67133 | 0.75315 | 0.54861 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | unilateral_step | TRUE | 2.35 | 4 | 4 | 3 | 1 | 3 | 5 | 3 | 3.2 | 2.65 | 2.65 | 2.9125 | 2.3875 | 0.50036 | 0.5006 | 0.5 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | unilateral_freeze | TRUE | 3.0625 | 2 | 3 | 1 | 3 | 1 | 2 | 2 | 2.25 | 1.9375 | 1.9375 | 1.9375 | 1.9375 | 0.93804 | 1.193 | 0.55556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | unilateral_spike | TRUE | 0.8 | 5 | 5 | 5 | 3 | 5 | 5 | 5 | 4.6 | 4.2 | 4.2 | 4.2 | 4.2 | 0.28757 | 0.34966 | 0.19444 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | distribution_location | TRUE | 2.35 | 1 | 5 | 5 | 3 | 5 | 1 | 1 | 3.2 | 2.65 | 2.65 | 2.65 | 2.65 | 1.1443 | 1.4581 | 0.67361 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | distribution_scale | TRUE | 0.95 | 5 | 5 | 4 | 3 | 4 | 5 | 5 | 4.4 | 4.05 | 4.05 | 4.05 | 4.05 | 0.28247 | 0.3319 | 0.20833 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | distribution_tail | TRUE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.29823 | 0.40909 | 0.13194 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | distribution_mixture | TRUE | 1.1 | 5 | 5 | 3 | 3 | 3 | 5 | 5 | 4.2 | 3.9 | 3.9 | 3.9 | 3.9 | 0.42816 | 0.496 | 0.32639 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | synchronous_switch | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.12897 | 0.10847 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | common_mode_drift | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 5 | 4.2 | 3.4 | 3.4 | 3.4 | 3.4 | 0.12897 | 0.10847 | 0.15972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | common_unequal | FALSE | 1.6 | 5 | 5 | 5 | 1 | 5 | 5 | 4 | 4.2 | 3.4 | 3.4 | 3.4 | 3.1375 | 0.38334 | 0.36113 | 0.41667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-17 | 2026-04-09 10:00 | opposite_direction | FALSE | 3.5125 | 1 | 2 | 3 | 1 | 3 | 1 | 1 | 1.65 | 1.4875 | 1.4875 | 1.4875 | 1.4875 | 1.3136 | 1.5782 | 0.91667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | baseline | FALSE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.28434 | 0.32112 | 0.22917 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | unilateral_drift | TRUE | 2.025 | 2 | 4 | 5 | 3 | 5 | 2 | 1 | 3.3 | 2.975 | 2.975 | 2.975 | 2.4625 | 0.95864 | 1.1579 | 0.65972 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | unilateral_step | TRUE | 1.4 | 4 | 4 | 4 | 3 | 4 | 4 | 3 | 3.8 | 3.6 | 3.6 | 3.6 | 3.3375 | 0.5556 | 0.62508 | 0.45139 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | unilateral_freeze | TRUE | 2.5375 | 4 | 3 | 1 | 3 | 1 | 3 | 5 | 2.95 | 2.4625 | 2.4625 | 2.2 | 2.725 | 0.55985 | 0.73865 | 0.29167 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | unilateral_spike | TRUE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.36045 | 0.45259 | 0.22222 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | distribution_location | TRUE | 2.5375 | 1 | 4 | 5 | 3 | 5 | 1 | 1 | 2.95 | 2.4625 | 2.4625 | 2.4625 | 2.4625 | 1.253 | 1.5236 | 0.84722 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | distribution_scale | TRUE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.18545 | 0.19796 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | distribution_tail | TRUE | 0.9875 | 5 | 4 | 5 | 3 | 5 | 5 | 5 | 4.35 | 4.0125 | 4.0125 | 4.0125 | 4.0125 | 0.3413 | 0.45773 | 0.16667 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | distribution_mixture | TRUE | 1.1 | 5 | 5 | 3 | 3 | 3 | 5 | 4 | 4.2 | 3.9 | 3.9 | 3.9 | 3.6375 | 0.42694 | 0.45231 | 0.38889 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | synchronous_switch | FALSE | 1.1 | 5 | 5 | 3 | 3 | 3 | 5 | 5 | 4.2 | 3.9 | 3.9 | 3.9 | 3.9 | 0.28054 | 0.3009 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | common_mode_drift | FALSE | 1.1 | 5 | 5 | 3 | 3 | 3 | 5 | 5 | 4.2 | 3.9 | 3.9 | 3.9 | 3.9 | 0.28054 | 0.3009 | 0.25 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | common_unequal | FALSE | 0 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4.4875 | 5 | 0.45714 | 0.55819 | 0.30556 | 0 | D4CAL-V16-e615cd349a49
PAIR_ORP13 | PAIR_ORP13-18 | 2026-04-13 16:00 | opposite_direction | FALSE | 3.1 | 1 | 1 | 5 | 3 | 5 | 1 | 1 | 2.2 | 1.9 | 1.9 | 1.9 | 1.9 | 1.8751 | 2.5557 | 0.85417 | 0 | D4CAL-V16-e615cd349a49

## roc_pr_curves
injection | curve | x | y | threshold | calibration_id
unilateral_drift | ROC | 0 | 0 | inf | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0 | 0.02381 | 3.7 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0 | 0.039683 | 3.6625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0 | 0.071429 | 3.55 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0 | 0.095238 | 3.5125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0 | 0.10317 | 3.475 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0 | 0.13492 | 3.4375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0 | 0.1746 | 3.4 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.0079365 | 0.1746 | 3.325 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.0079365 | 0.19048 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.015873 | 0.22222 | 3.25 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.015873 | 0.23016 | 3.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.015873 | 0.24603 | 3.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.015873 | 0.25397 | 3.175 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.015873 | 0.26984 | 3.1375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.015873 | 0.30159 | 3.1375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.031746 | 0.31746 | 3.1 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.039683 | 0.33333 | 3.0625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.039683 | 0.34127 | 3.025 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.047619 | 0.34921 | 3 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.055556 | 0.34921 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.055556 | 0.37302 | 2.9125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.079365 | 0.4127 | 2.875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.087302 | 0.45238 | 2.85 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.087302 | 0.46825 | 2.8125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.10317 | 0.46825 | 2.7375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.11111 | 0.48413 | 2.725 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.11111 | 0.49206 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.11905 | 0.53968 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.12698 | 0.57143 | 2.6875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.13492 | 0.5873 | 2.6625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.13492 | 0.60317 | 2.6125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.14286 | 0.60317 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.14286 | 0.61111 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.15079 | 0.61111 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.15873 | 0.66667 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.16667 | 0.66667 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.1746 | 0.69048 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.1746 | 0.70635 | 2.4625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.1746 | 0.71429 | 2.4625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.1746 | 0.75397 | 2.4 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.1746 | 0.7619 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.18254 | 0.80159 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.18254 | 0.80952 | 2.35 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.19048 | 0.80952 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.19048 | 0.8254 | 2.25 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.20635 | 0.84127 | 2.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.21429 | 0.84127 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.22222 | 0.85714 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.23016 | 0.88095 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.2381 | 0.88095 | 2.125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.24603 | 0.88889 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.24603 | 0.90476 | 2.0625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.24603 | 0.9127 | 2.05 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.24603 | 0.92857 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.25397 | 0.92857 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.25397 | 0.94444 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.2619 | 0.94444 | 1.95 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.27778 | 0.94444 | 1.9375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.30159 | 0.94444 | 1.9125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.30952 | 0.94444 | 1.9 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.3254 | 0.94444 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.33333 | 0.94444 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.33333 | 0.95238 | 1.85 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.33333 | 0.97619 | 1.8375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.34127 | 0.97619 | 1.8125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.35714 | 0.97619 | 1.75 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.36508 | 0.97619 | 1.7375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.38889 | 0.97619 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.4127 | 0.97619 | 1.6625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.44444 | 0.97619 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.47619 | 0.97619 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.48413 | 0.98413 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.50794 | 0.98413 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.53175 | 0.98413 | 1.4625 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.53175 | 0.99206 | 1.4375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.53968 | 0.99206 | 1.3875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.56349 | 0.99206 | 1.35 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.57937 | 0.99206 | 1.325 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.60317 | 0.99206 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.61905 | 0.99206 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.65873 | 0.99206 | 1.2 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.66667 | 0.99206 | 1.1375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.71429 | 0.99206 | 1.025 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.74603 | 0.99206 | 0.9875 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.76984 | 0.99206 | 0.95 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.78571 | 0.99206 | 0.8125 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.84127 | 0.99206 | 0.8 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.84921 | 0.99206 | 0.7375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.9127 | 0.99206 | 0.55 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.92063 | 0.99206 | 0.4375 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 0.96825 | 0.99206 | 0.4 | D4CAL-V16-e615cd349a49
unilateral_drift | ROC | 1 | 1 | 0 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 1 | 0.5 | 0 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.50607 | 0.4 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.51867 | 0.4375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.52083 | 0.55 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.52966 | 0.5875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.53879 | 0.7375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.54113 | 0.8 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.55804 | 0.8125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.56054 | 0.85 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.56306 | 0.95 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.57078 | 0.9875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.5814 | 1.025 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.58685 | 1.0625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.59242 | 1.1 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.59809 | 1.1375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.60096 | 1.2 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.61576 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.62189 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.625 | 1.2875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.62814 | 1.3125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.63131 | 1.325 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.63776 | 1.35 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.64767 | 1.3875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.99206 | 0.65104 | 1.4375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.98413 | 0.64921 | 1.4625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.98413 | 0.65957 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.98413 | 0.6631 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.98413 | 0.66667 | 1.5125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.98413 | 0.67027 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.67213 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.67582 | 1.55 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.67956 | 1.575 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.68333 | 1.6 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.68715 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.69492 | 1.65 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.70286 | 1.6625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.7069 | 1.6875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.71098 | 1.7 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.71512 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.72781 | 1.7375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.73214 | 1.75 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.74096 | 1.8125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.97619 | 0.74545 | 1.8375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.95238 | 0.74074 | 1.85 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.94444 | 0.73913 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.94444 | 0.74375 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.94444 | 0.75316 | 1.9 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.94444 | 0.75796 | 1.9125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.94444 | 0.77273 | 1.9375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.94444 | 0.78289 | 1.95 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.94444 | 0.78808 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.93651 | 0.78667 | 2 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.92857 | 0.78523 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.92857 | 0.79054 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.9127 | 0.78767 | 2.05 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.90476 | 0.78621 | 2.0625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.88889 | 0.78322 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.88095 | 0.78723 | 2.125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.88095 | 0.79286 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.85714 | 0.79412 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.84127 | 0.79699 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.84127 | 0.80303 | 2.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.8254 | 0.8125 | 2.25 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.80952 | 0.80952 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.80952 | 0.816 | 2.35 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.80159 | 0.81452 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.7619 | 0.81356 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.75397 | 0.81197 | 2.4 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.71429 | 0.80357 | 2.4625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.70635 | 0.8018 | 2.4625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.69048 | 0.79817 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.66667 | 0.8 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.66667 | 0.80769 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.61111 | 0.80208 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.61111 | 0.81053 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.60317 | 0.80851 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.60317 | 0.8172 | 2.6125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.59524 | 0.81522 | 2.6125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.5873 | 0.81319 | 2.6625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.57143 | 0.81818 | 2.6875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.53968 | 0.81928 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.49206 | 0.81579 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.48413 | 0.81333 | 2.725 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.46825 | 0.81944 | 2.7375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.46825 | 0.84286 | 2.8125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.46032 | 0.84058 | 2.8375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.45238 | 0.83824 | 2.85 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.4127 | 0.83871 | 2.875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.37302 | 0.87037 | 2.9125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.34921 | 0.86275 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.34921 | 0.88 | 3 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.34127 | 0.89583 | 3.025 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.33333 | 0.89362 | 3.0625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.31746 | 0.90909 | 3.1 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.30159 | 0.95 | 3.1375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.26984 | 0.94444 | 3.1375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.25397 | 0.94118 | 3.175 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.24603 | 0.93939 | 3.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.23016 | 0.93548 | 3.2125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.22222 | 0.93333 | 3.25 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.19048 | 0.96 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.18254 | 0.95833 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.1746 | 0.95652 | 3.325 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.1746 | 1 | 3.4 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.13492 | 1 | 3.4375 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.10317 | 1 | 3.475 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.095238 | 1 | 3.5125 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.071429 | 1 | 3.55 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.039683 | 1 | 3.6625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.031746 | 1 | 3.6625 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0.02381 | 1 | 3.7 | D4CAL-V16-e615cd349a49
unilateral_drift | PR | 0 | 1 |  | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0 | 0 | inf | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0 | 0.0079365 | 4 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0 | 0.055556 | 3.4375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0 | 0.071429 | 3.4 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0 | 0.11111 | 3.4 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0 | 0.12698 | 3.3625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.0079365 | 0.14286 | 3.325 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.0079365 | 0.15079 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.0079365 | 0.16667 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.015873 | 0.18254 | 3.25 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.015873 | 0.19841 | 3.2125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.015873 | 0.20635 | 3.175 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.031746 | 0.22222 | 3.1 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.039683 | 0.2381 | 3.0625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.047619 | 0.28571 | 3 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.055556 | 0.28571 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.055556 | 0.29365 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.055556 | 0.31746 | 2.95 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.055556 | 0.3254 | 2.9125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.079365 | 0.34127 | 2.875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.087302 | 0.38095 | 2.85 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.087302 | 0.40476 | 2.8375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.087302 | 0.43651 | 2.8125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.087302 | 0.44444 | 2.7625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.10317 | 0.44444 | 2.7375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.11111 | 0.45238 | 2.725 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.11905 | 0.47619 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.12698 | 0.47619 | 2.6875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.13492 | 0.48413 | 2.6625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.13492 | 0.5 | 2.625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.13492 | 0.55556 | 2.5875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.15079 | 0.57143 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.15873 | 0.59524 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.1746 | 0.59524 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.1746 | 0.62698 | 2.475 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.1746 | 0.6746 | 2.4 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.1746 | 0.68254 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.18254 | 0.70635 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.18254 | 0.72222 | 2.325 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.19048 | 0.7381 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.19048 | 0.7619 | 2.25 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.20635 | 0.77778 | 2.2125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.21429 | 0.77778 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.22222 | 0.78571 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.23016 | 0.80159 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.23016 | 0.81746 | 2.1375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.23016 | 0.8254 | 2.1375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.2381 | 0.8254 | 2.125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.2381 | 0.84127 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.25397 | 0.84127 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.25397 | 0.85714 | 2 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.2619 | 0.85714 | 1.95 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.27778 | 0.85714 | 1.9375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.30159 | 0.86508 | 1.9125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.30952 | 0.86508 | 1.9 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.3254 | 0.86508 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.33333 | 0.86508 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.33333 | 0.88095 | 1.8375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.34127 | 0.88889 | 1.8125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.35714 | 0.88889 | 1.75 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.36508 | 0.88889 | 1.7375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.38889 | 0.89683 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.39683 | 0.89683 | 1.7 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.4127 | 0.9127 | 1.6625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.44444 | 0.9127 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.45238 | 0.9127 | 1.6 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.45238 | 0.92063 | 1.5875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.46032 | 0.92063 | 1.575 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.46032 | 0.92857 | 1.55 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.46825 | 0.93651 | 1.55 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.48413 | 0.93651 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.49206 | 0.94444 | 1.5125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.50794 | 0.94444 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.53175 | 0.94444 | 1.4625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.53175 | 0.95238 | 1.4 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.53968 | 0.95238 | 1.3875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.53968 | 0.96825 | 1.3625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.56349 | 0.96825 | 1.35 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.57937 | 0.96825 | 1.325 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.60317 | 0.96825 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.61905 | 0.96825 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.65873 | 0.96825 | 1.2 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.66667 | 0.97619 | 1.1375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.71429 | 0.97619 | 1.025 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.74603 | 0.97619 | 0.9875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.76984 | 0.97619 | 0.95 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.77778 | 0.98413 | 0.85 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.78571 | 0.98413 | 0.8125 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.84127 | 0.98413 | 0.8 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.84921 | 0.98413 | 0.7375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.84921 | 0.99206 | 0.6625 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.88095 | 0.99206 | 0.5875 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.9127 | 1 | 0.55 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.92063 | 1 | 0.4375 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 0.96825 | 1 | 0.4 | D4CAL-V16-e615cd349a49
unilateral_step | ROC | 1 | 1 | 0 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 1 | 0.5 | 0 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 1 | 0.50806 | 0.4 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 1 | 0.52066 | 0.4375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 1 | 0.52282 | 0.55 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.99206 | 0.52966 | 0.5875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.99206 | 0.53879 | 0.6625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.98413 | 0.5368 | 0.7375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.98413 | 0.53913 | 0.8 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.98413 | 0.55605 | 0.8125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.98413 | 0.55856 | 0.85 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.97619 | 0.55909 | 0.95 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.97619 | 0.56682 | 0.9875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.97619 | 0.57746 | 1.025 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.97619 | 0.58294 | 1.0625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.97619 | 0.58852 | 1.1 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.97619 | 0.5942 | 1.1375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96825 | 0.59512 | 1.2 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96825 | 0.61 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96825 | 0.61616 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96825 | 0.61929 | 1.2875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96825 | 0.62245 | 1.3125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96825 | 0.62564 | 1.325 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96825 | 0.63212 | 1.35 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96825 | 0.64211 | 1.3625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.96032 | 0.64021 | 1.3625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.95238 | 0.6383 | 1.3875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.95238 | 0.64171 | 1.4 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.94444 | 0.63978 | 1.4625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.94444 | 0.65027 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.94444 | 0.65385 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.94444 | 0.65746 | 1.5125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.93651 | 0.65922 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.93651 | 0.66292 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.93651 | 0.66667 | 1.55 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.92857 | 0.66857 | 1.55 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.92063 | 0.66667 | 1.575 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.92063 | 0.67052 | 1.5875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.9127 | 0.6686 | 1.6 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.9127 | 0.67251 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.9127 | 0.68047 | 1.65 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.9127 | 0.68862 | 1.6625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.90476 | 0.69091 | 1.6875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.89683 | 0.69325 | 1.7 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.89683 | 0.69753 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.88889 | 0.70886 | 1.7375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.88889 | 0.71338 | 1.75 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.88889 | 0.72258 | 1.8125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.88095 | 0.72549 | 1.8375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.87302 | 0.72368 | 1.85 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.86508 | 0.72185 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.86508 | 0.72667 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.86508 | 0.73649 | 1.9 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.86508 | 0.7415 | 1.9125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.85714 | 0.75524 | 1.9375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.85714 | 0.76596 | 1.95 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.85714 | 0.77143 | 2 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.84127 | 0.76812 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.84127 | 0.77372 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.84127 | 0.77941 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.8254 | 0.77612 | 2.125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.8254 | 0.78195 | 2.1375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.81746 | 0.7803 | 2.1375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.80159 | 0.77692 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.78571 | 0.77953 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.77778 | 0.784 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.77778 | 0.79032 | 2.2125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.7619 | 0.8 | 2.25 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.7381 | 0.79487 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.72222 | 0.79825 | 2.325 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.71429 | 0.79646 | 2.35 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.70635 | 0.79464 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.68254 | 0.7963 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.6746 | 0.79439 | 2.4 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.65873 | 0.79048 | 2.4375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.64286 | 0.78641 | 2.4625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.62698 | 0.78218 | 2.475 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.61905 | 0.78 | 2.475 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.61111 | 0.77778 | 2.5125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.60317 | 0.77551 | 2.5125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.59524 | 0.7732 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.59524 | 0.78125 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.59524 | 0.78947 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.57143 | 0.79121 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.56349 | 0.79775 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.55556 | 0.8046 | 2.5875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.5 | 0.7875 | 2.625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.49206 | 0.78481 | 2.65 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.48413 | 0.78205 | 2.6625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.47619 | 0.78947 | 2.6875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.47619 | 0.8 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.45238 | 0.80282 | 2.725 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.44444 | 0.81159 | 2.7375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.44444 | 0.83582 | 2.7625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.43651 | 0.83333 | 2.8125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.40476 | 0.82258 | 2.8375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.38095 | 0.81356 | 2.85 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.34127 | 0.81132 | 2.875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.3254 | 0.85417 | 2.9125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.31746 | 0.85106 | 2.95 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.29365 | 0.84091 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.28571 | 0.83721 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.28571 | 0.85714 | 3 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.2381 | 0.85714 | 3.0625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.22222 | 0.875 | 3.1 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.20635 | 0.92857 | 3.175 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.19841 | 0.92593 | 3.2125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.18254 | 0.92 | 3.25 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.16667 | 0.95455 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.15079 | 0.95 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.14286 | 0.94737 | 3.325 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.12698 | 1 | 3.3625 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.11111 | 1 | 3.4 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.071429 | 1 | 3.4 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.055556 | 1 | 3.4375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.047619 | 1 | 3.475 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.039683 | 1 | 3.5875 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.031746 | 1 | 3.7375 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.02381 | 1 | 3.8125 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.015873 | 1 | 3.85 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0.0079365 | 1 | 4 | D4CAL-V16-e615cd349a49
unilateral_step | PR | 0 | 1 |  | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0 | 0 | inf | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0 | 0.0079365 | 3.85 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0 | 0.031746 | 3.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0 | 0.063492 | 3.4375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0 | 0.079365 | 3.3625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.0079365 | 0.079365 | 3.325 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.0079365 | 0.087302 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.015873 | 0.10317 | 3.25 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.015873 | 0.11111 | 3.2125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.015873 | 0.12698 | 3.1375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.031746 | 0.13492 | 3.1 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.039683 | 0.14286 | 3.0625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.055556 | 0.14286 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.055556 | 0.16667 | 2.95 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.055556 | 0.1746 | 2.9125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.079365 | 0.19048 | 2.875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.087302 | 0.19048 | 2.85 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.087302 | 0.22222 | 2.8375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.087302 | 0.23016 | 2.8125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.087302 | 0.25397 | 2.7625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.10317 | 0.26984 | 2.7375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.11111 | 0.27778 | 2.725 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.11905 | 0.27778 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.12698 | 0.30952 | 2.6875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.13492 | 0.30952 | 2.6625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.13492 | 0.31746 | 2.625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.14286 | 0.3254 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.15079 | 0.34127 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.16667 | 0.34127 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.1746 | 0.36508 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.1746 | 0.37302 | 2.5 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.1746 | 0.40476 | 2.3875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.18254 | 0.4127 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.18254 | 0.42063 | 2.35 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.18254 | 0.47619 | 2.35 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.18254 | 0.5 | 2.325 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.18254 | 0.50794 | 2.3125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.19048 | 0.51587 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.19048 | 0.54762 | 2.25 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.20635 | 0.56349 | 2.2125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.21429 | 0.57937 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.2381 | 0.57937 | 2.125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.2381 | 0.5873 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.24603 | 0.5873 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.24603 | 0.59524 | 2.0625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.24603 | 0.61905 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.25397 | 0.61905 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.25397 | 0.63492 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.2619 | 0.64286 | 1.95 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.27778 | 0.64286 | 1.9375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.30159 | 0.68254 | 1.9125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.30952 | 0.68254 | 1.9 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.3254 | 0.69048 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.33333 | 0.69048 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.33333 | 0.71429 | 1.8375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.34127 | 0.72222 | 1.8125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.35714 | 0.72222 | 1.75 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.36508 | 0.72222 | 1.7375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.38889 | 0.74603 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.38889 | 0.75397 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.39683 | 0.7619 | 1.7 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.40476 | 0.7619 | 1.6875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.4127 | 0.76984 | 1.6625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.42857 | 0.77778 | 1.65 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.42857 | 0.78571 | 1.625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.44444 | 0.78571 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.45238 | 0.79365 | 1.6 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.46032 | 0.79365 | 1.575 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.46825 | 0.80159 | 1.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.47619 | 0.80159 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.48413 | 0.8254 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.49206 | 0.83333 | 1.5125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.50794 | 0.83333 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.53175 | 0.85714 | 1.4625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.53175 | 0.86508 | 1.4375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.53968 | 0.87302 | 1.3875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.56349 | 0.87302 | 1.35 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.57937 | 0.87302 | 1.325 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.59524 | 0.87302 | 1.2875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.60317 | 0.88095 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.61905 | 0.88095 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.65873 | 0.88889 | 1.2 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.65873 | 0.89683 | 1.175 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.66667 | 0.89683 | 1.1375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.68254 | 0.89683 | 1.1 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.69841 | 0.92063 | 1.0625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.71429 | 0.92063 | 1.025 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.74603 | 0.92063 | 0.9875 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.76984 | 0.92857 | 0.95 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.77778 | 0.93651 | 0.85 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.78571 | 0.93651 | 0.8125 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.84127 | 0.96032 | 0.8 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.84921 | 0.96032 | 0.7375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.84921 | 0.96825 | 0.6625 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.9127 | 0.96825 | 0.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.92063 | 0.96825 | 0.4375 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 0.96825 | 0.98413 | 0.4 | D4CAL-V16-e615cd349a49
unilateral_freeze | ROC | 1 | 1 | 0 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 1 | 0.5 | 0 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.98413 | 0.50407 | 0.4 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.96825 | 0.51261 | 0.4375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.96825 | 0.51477 | 0.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.96825 | 0.52361 | 0.5875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.96825 | 0.53275 | 0.6625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.96032 | 0.5307 | 0.7375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.96032 | 0.53304 | 0.8 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.93651 | 0.54378 | 0.8125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.93651 | 0.5463 | 0.85 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.92857 | 0.54673 | 0.95 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.92063 | 0.55238 | 0.9875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.92063 | 0.56311 | 1.025 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.92063 | 0.56863 | 1.0625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.89683 | 0.56784 | 1.1 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.89683 | 0.5736 | 1.1375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.89683 | 0.57653 | 1.175 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.88889 | 0.57436 | 1.2 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.88095 | 0.5873 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.88095 | 0.59358 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.87302 | 0.59459 | 1.2875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.87302 | 0.59783 | 1.3125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.87302 | 0.60109 | 1.325 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.87302 | 0.60773 | 1.35 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.87302 | 0.61798 | 1.3875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.86508 | 0.61932 | 1.4375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.85714 | 0.61714 | 1.4625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.83333 | 0.6213 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.83333 | 0.625 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.83333 | 0.62874 | 1.5125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.8254 | 0.6303 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.80159 | 0.62733 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.80159 | 0.63125 | 1.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.79365 | 0.63291 | 1.575 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.79365 | 0.63694 | 1.6 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.78571 | 0.63871 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.78571 | 0.64706 | 1.625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.77778 | 0.64474 | 1.65 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.76984 | 0.65101 | 1.6625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.7619 | 0.65306 | 1.6875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.7619 | 0.65753 | 1.7 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.75397 | 0.65972 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.74603 | 0.65734 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.72222 | 0.66423 | 1.7375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.72222 | 0.66912 | 1.75 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.72222 | 0.6791 | 1.8125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.71429 | 0.68182 | 1.8375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.69048 | 0.67442 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.69048 | 0.67969 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.68254 | 0.688 | 1.9 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.68254 | 0.69355 | 1.9125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.64286 | 0.69828 | 1.9375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.64286 | 0.71053 | 1.95 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.63492 | 0.71429 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.62698 | 0.71171 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.61905 | 0.70909 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.61905 | 0.7156 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.59524 | 0.70755 | 2.0625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.5873 | 0.70476 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.5873 | 0.71154 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.57937 | 0.70874 | 2.125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.57937 | 0.71569 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.57937 | 0.72277 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.57937 | 0.73 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.56349 | 0.73196 | 2.2125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.54762 | 0.74194 | 2.25 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.53175 | 0.73626 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.51587 | 0.73034 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.50794 | 0.73563 | 2.3125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.5 | 0.73256 | 2.325 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.47619 | 0.72289 | 2.35 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.42063 | 0.69737 | 2.35 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.4127 | 0.69333 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.40476 | 0.69863 | 2.3875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.38889 | 0.69014 | 2.425 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.37302 | 0.68116 | 2.5 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.36508 | 0.67647 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.34127 | 0.67188 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.34127 | 0.68254 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.34127 | 0.69355 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.3254 | 0.69492 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.31746 | 0.70175 | 2.625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.30952 | 0.69643 | 2.6625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.30952 | 0.70909 | 2.6875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.27778 | 0.7 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.27778 | 0.71429 | 2.725 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.26984 | 0.7234 | 2.7375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.25397 | 0.74419 | 2.7625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.23016 | 0.725 | 2.8125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.22222 | 0.71795 | 2.8375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.19048 | 0.68571 | 2.85 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.19048 | 0.70588 | 2.875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.1746 | 0.75862 | 2.9125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.16667 | 0.75 | 2.95 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.14286 | 0.72 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.14286 | 0.75 | 3 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.14286 | 0.78261 | 3.0625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.13492 | 0.80952 | 3.1 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.12698 | 0.88889 | 3.1375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.11111 | 0.875 | 3.2125 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.10317 | 0.86667 | 3.25 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.087302 | 0.91667 | 3.2875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.079365 | 0.90909 | 3.325 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.079365 | 1 | 3.3625 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.071429 | 1 | 3.4 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.063492 | 1 | 3.4375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.031746 | 1 | 3.55 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.02381 | 1 | 3.5875 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.015873 | 1 | 3.7375 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0.0079365 | 1 | 3.85 | D4CAL-V16-e615cd349a49
unilateral_freeze | PR | 0 | 1 |  | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0 | 0 | inf | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0 | 0.0079365 | 3.5125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.0079365 | 0.02381 | 3.325 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.015873 | 0.031746 | 3.25 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.015873 | 0.047619 | 3.1375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.031746 | 0.055556 | 3.1 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.047619 | 0.055556 | 3 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.055556 | 0.063492 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.055556 | 0.071429 | 2.95 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.079365 | 0.079365 | 2.875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.087302 | 0.079365 | 2.85 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.087302 | 0.10317 | 2.8 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.10317 | 0.11905 | 2.7375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.11111 | 0.12698 | 2.725 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.12698 | 0.12698 | 2.6875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.13492 | 0.14286 | 2.6625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.14286 | 0.14286 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.15079 | 0.15079 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.15873 | 0.16667 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.16667 | 0.1746 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.1746 | 0.1746 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.1746 | 0.19841 | 2.425 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.18254 | 0.19841 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.18254 | 0.20635 | 2.325 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.19048 | 0.20635 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.19048 | 0.21429 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.20635 | 0.23016 | 2.2125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.21429 | 0.24603 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.21429 | 0.25397 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.22222 | 0.2619 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.23016 | 0.28571 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.23016 | 0.30159 | 2.1375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.23016 | 0.30952 | 2.1375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.2381 | 0.30952 | 2.125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.24603 | 0.31746 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.24603 | 0.33333 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.25397 | 0.33333 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.25397 | 0.34921 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.25397 | 0.36508 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.2619 | 0.36508 | 1.95 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.27778 | 0.36508 | 1.9375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.30159 | 0.38095 | 1.9125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.30952 | 0.38095 | 1.9 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.3254 | 0.38889 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.33333 | 0.40476 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.33333 | 0.4127 | 1.8625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.34127 | 0.4127 | 1.8125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.34127 | 0.42063 | 1.8 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.35714 | 0.43651 | 1.75 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.36508 | 0.43651 | 1.7375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.38889 | 0.46032 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.38889 | 0.47619 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.40476 | 0.47619 | 1.6875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.4127 | 0.48413 | 1.6625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.42857 | 0.49206 | 1.65 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.44444 | 0.49206 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.44444 | 0.5 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.45238 | 0.5 | 1.6 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.45238 | 0.50794 | 1.5875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.47619 | 0.50794 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.48413 | 0.51587 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.49206 | 0.51587 | 1.5125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.5 | 0.52381 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.50794 | 0.54762 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.53175 | 0.57937 | 1.4625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.53175 | 0.59524 | 1.4 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.53968 | 0.61111 | 1.3875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.53968 | 0.61905 | 1.3625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.53968 | 0.63492 | 1.3625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.56349 | 0.63492 | 1.35 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.57937 | 0.66667 | 1.325 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.59524 | 0.69841 | 1.2875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.60317 | 0.69841 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.61905 | 0.71429 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.65873 | 0.74603 | 1.2 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.65873 | 0.75397 | 1.175 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.66667 | 0.75397 | 1.1375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.68254 | 0.75397 | 1.1 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.69841 | 0.78571 | 1.0625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.71429 | 0.78571 | 1.025 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.71429 | 0.79365 | 1 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.74603 | 0.81746 | 0.9875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.76984 | 0.8254 | 0.95 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.77778 | 0.83333 | 0.85 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.78571 | 0.84921 | 0.8125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.84127 | 0.89683 | 0.8 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.84921 | 0.89683 | 0.7375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.84921 | 0.90476 | 0.7 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.84921 | 0.92063 | 0.6625 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.88095 | 0.94444 | 0.5875 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.9127 | 0.94444 | 0.55 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.9127 | 0.95238 | 0.5125 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.92063 | 0.95238 | 0.4375 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 0.96825 | 0.98413 | 0.4 | D4CAL-V16-e615cd349a49
unilateral_spike | ROC | 1 | 1 | 0 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 1 | 0.5 | 0 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.98413 | 0.50407 | 0.4 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.95238 | 0.50847 | 0.4375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.95238 | 0.51064 | 0.5125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.94444 | 0.50855 | 0.55 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.94444 | 0.51739 | 0.5875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.92063 | 0.52018 | 0.6625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.90476 | 0.51584 | 0.7 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.89683 | 0.51364 | 0.7375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.89683 | 0.51598 | 0.8 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.84921 | 0.51942 | 0.8125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.83333 | 0.51724 | 0.85 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.8254 | 0.51741 | 0.95 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.81746 | 0.52284 | 0.9875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.79365 | 0.52632 | 1 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.78571 | 0.52381 | 1.025 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.78571 | 0.52941 | 1.0625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.75397 | 0.52486 | 1.1 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.75397 | 0.53073 | 1.1375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.75397 | 0.53371 | 1.175 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.74603 | 0.53107 | 1.2 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.71429 | 0.53571 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.69841 | 0.53659 | 1.2125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.69841 | 0.53988 | 1.2875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.68254 | 0.5375 | 1.3125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.66667 | 0.53503 | 1.325 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.63492 | 0.5298 | 1.35 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.63492 | 0.54054 | 1.3625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.61905 | 0.53425 | 1.3625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.61111 | 0.53103 | 1.3875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.59524 | 0.52817 | 1.4 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.57937 | 0.52143 | 1.4625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.54762 | 0.5188 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.52381 | 0.51163 | 1.475 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.51587 | 0.51181 | 1.5125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.51587 | 0.51587 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.50794 | 0.51613 | 1.5375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.50794 | 0.52033 | 1.55 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.50794 | 0.52459 | 1.575 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.50794 | 0.52893 | 1.5875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.5 | 0.525 | 1.6 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.5 | 0.52941 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.49206 | 0.52542 | 1.6125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.49206 | 0.53448 | 1.65 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.48413 | 0.53982 | 1.6625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.47619 | 0.54054 | 1.6875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.47619 | 0.54545 | 1.7 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.47619 | 0.55046 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.46032 | 0.54206 | 1.725 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.43651 | 0.54455 | 1.7375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.43651 | 0.55 | 1.75 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.42063 | 0.55208 | 1.8 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.4127 | 0.54737 | 1.8125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.4127 | 0.55319 | 1.8625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.40476 | 0.54839 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.38889 | 0.54444 | 1.875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.38095 | 0.55172 | 1.9 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.38095 | 0.55814 | 1.9125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.36508 | 0.5679 | 1.9375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.36508 | 0.58228 | 1.95 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.36508 | 0.58974 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.34921 | 0.57895 | 1.9875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.34127 | 0.57333 | 2.0125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.33333 | 0.56757 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.33333 | 0.57534 | 2.025 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.3254 | 0.56944 | 2.0625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.31746 | 0.56338 | 2.1 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.30952 | 0.56522 | 2.125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.30952 | 0.57353 | 2.1375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.30159 | 0.56716 | 2.1375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.28571 | 0.55385 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.2619 | 0.54098 | 2.175 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.25397 | 0.54237 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.24603 | 0.53448 | 2.2 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.23016 | 0.52727 | 2.2125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.21429 | 0.52941 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.20635 | 0.52 | 2.2875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.20635 | 0.53061 | 2.325 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.19841 | 0.52083 | 2.3625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.19841 | 0.53191 | 2.425 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.19048 | 0.52174 | 2.475 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.18254 | 0.51111 | 2.5125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.1746 | 0.5 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.1746 | 0.51163 | 2.5375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.16667 | 0.5122 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.15079 | 0.5 | 2.55 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.14286 | 0.5 | 2.575 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.14286 | 0.51429 | 2.6625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.12698 | 0.5 | 2.6875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.12698 | 0.51613 | 2.7 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.12698 | 0.53333 | 2.725 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.11905 | 0.53571 | 2.7375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.10317 | 0.54167 | 2.8 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.095238 | 0.52174 | 2.8125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.087302 | 0.5 | 2.8375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.079365 | 0.47619 | 2.85 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.079365 | 0.5 | 2.875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.071429 | 0.5625 | 2.95 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.063492 | 0.53333 | 2.9875 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.055556 | 0.53846 | 3 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.055556 | 0.58333 | 3.0625 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.055556 | 0.63636 | 3.1 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.047619 | 0.75 | 3.1375 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.031746 | 0.66667 | 3.25 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.02381 | 0.75 | 3.325 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0.0079365 | 1 | 3.5125 | D4CAL-V16-e615cd349a49
unilateral_spike | PR | 0 | 1 |  | D4CAL-V16-e615cd349a49

## ablation
condition | ROC_AUC | AUC_CI_low | AUC_CI_high | synchronous_FAR | FAR_CI_low | FAR_CI_high | AUC_process_time_blocks | FAR_process_time_blocks | bootstrap_unit | n_positive | n_negative | calibration_id
full | 0.74969 | 0.71712 | 0.7891 | 0.031915 | 0 | 0.060241 | 11 | 11 | synchronized_7d_process_time_block_all_pairs | 504 | 126 | D4CAL-V16-e615cd349a49
no_dist | 0.65327 | 0.61456 | 0.6956 | 0.069767 | 0.023796 | 0.12504 | 11 | 11 | synchronized_7d_process_time_block_all_pairs | 504 | 126 | D4CAL-V16-e615cd349a49
no_trend | 0.75225 | 0.71969 | 0.79408 | 0.093023 | 0.038449 | 0.14867 | 11 | 11 | synchronized_7d_process_time_block_all_pairs | 504 | 126 | D4CAL-V16-e615cd349a49
no_var | 0.7554 | 0.72782 | 0.79752 | 0.010309 | 0 | 0.035747 | 11 | 11 | synchronized_7d_process_time_block_all_pairs | 504 | 126 | D4CAL-V16-e615cd349a49
no_cp | 0.75944 | 0.7244 | 0.79845 | 0.030928 | 0 | 0.065793 | 11 | 11 | synchronized_7d_process_time_block_all_pairs | 504 | 126 | D4CAL-V16-e615cd349a49
no_deadband | 0.74969 | 0.71913 | 0.78775 | 0.031915 | 0.0090829 | 0.057493 | 11 | 11 | synchronized_7d_process_time_block_all_pairs | 504 | 126 | D4CAL-V16-e615cd349a49

## distribution_internal_ablation
challenge | alternative | metric | full_value | alternative_value | difference | CI_low | CI_high | n_window_clusters | n_process_time_blocks | bootstrap_unit | decision_scope | calibration_id
distribution_location | W1-only | delta_AUROC_full_minus_alternative | 0.86524 | 0.87018 | -0.0049446 | -0.013386 | 0.0033079 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_location | W1-only | delta_AUPRC_full_minus_alternative | 0.80289 | 0.80729 | -0.0044069 | -0.013265 | 0.0042283 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_location | KS-only | delta_AUROC_full_minus_alternative | 0.86524 | 0.85784 | 0.0074011 | -0.00094105 | 0.014981 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_location | KS-only | delta_AUPRC_full_minus_alternative | 0.80289 | 0.80204 | 0.00085259 | -0.016385 | 0.015789 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_scale | W1-only | delta_AUROC_full_minus_alternative | 0.56431 | 0.57281 | -0.0085034 | -0.020869 | 0.0028867 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_scale | W1-only | delta_AUPRC_full_minus_alternative | 0.56461 | 0.56816 | -0.0035508 | -0.014336 | 0.0033664 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_scale | KS-only | delta_AUROC_full_minus_alternative | 0.56431 | 0.53319 | 0.031116 | 0.020648 | 0.042431 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_scale | KS-only | delta_AUPRC_full_minus_alternative | 0.56461 | 0.53331 | 0.031296 | 0.017666 | 0.04402 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_tail | W1-only | delta_AUROC_full_minus_alternative | 0.59152 | 0.63228 | -0.040753 | -0.057986 | -0.026168 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_tail | W1-only | delta_AUPRC_full_minus_alternative | 0.5848 | 0.6147 | -0.029906 | -0.046995 | -0.016542 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_tail | KS-only | delta_AUROC_full_minus_alternative | 0.59152 | 0.47714 | 0.11439 | 0.096012 | 0.14114 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_tail | KS-only | delta_AUPRC_full_minus_alternative | 0.5848 | 0.48469 | 0.1001 | 0.084444 | 0.12457 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_mixture | W1-only | delta_AUROC_full_minus_alternative | 0.71312 | 0.70279 | 0.01033 | 0.0029895 | 0.020002 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_mixture | W1-only | delta_AUPRC_full_minus_alternative | 0.62555 | 0.61841 | 0.0071382 | -0.00082776 | 0.014465 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_mixture | KS-only | delta_AUROC_full_minus_alternative | 0.71312 | 0.72276 | -0.0096372 | -0.024787 | 0.003377 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
distribution_mixture | KS-only | delta_AUPRC_full_minus_alternative | 0.62555 | 0.63147 | -0.0059257 | -0.020829 | 0.0080436 | 126 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_construct_ablation | D4CAL-V16-e615cd349a49
equal_common_mode_control | Full | conditional_new_FAR_common_eligible_set |  | 0.033333 |  | 0 | 0.06317 | 90 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_negative_control | D4CAL-V16-e615cd349a49
equal_common_mode_control | W1-only | conditional_new_FAR_common_eligible_set |  | 0.033333 |  | 0 | 0.060976 | 90 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_negative_control | D4CAL-V16-e615cd349a49
equal_common_mode_control | KS-only | conditional_new_FAR_common_eligible_set |  | 0.033333 |  | 0.010199 | 0.0625 | 90 | 11 | synchronized_7d_process_time_block_all_pairs | internal_validation_negative_control | D4CAL-V16-e615cd349a49

## common_change_contract
scenario | injection | role | metric | estimate | ci95_low | ci95_high | n_window_clusters | n_process_time_blocks | bootstrap_unit | alarm_threshold | acceptance_target | pass | claim_scope | calibration_id
common_equal | common_mode_drift | negative_control | conditional_false_alarm_rate | 0.031915 | 0.0098916 | 0.057151 | 94 | 11 | synchronized_7d_process_time_block_all_pairs | 3 | 0.1 | TRUE | equal change contributes to conditional FAR; unequal and opposite changes are positive asymmetry stress tests and never enter FAR | D4CAL-V16-e615cd349a49
common_unequal | common_unequal | positive_asymmetry_stress_test | conditional_response_rate | 0.45745 | 0.35287 | 0.6 | 94 | 11 | synchronized_7d_process_time_block_all_pairs | 3 |  |  | equal change contributes to conditional FAR; unequal and opposite changes are positive asymmetry stress tests and never enter FAR | D4CAL-V16-e615cd349a49
opposite_direction | opposite_direction | positive_asymmetry_stress_test | conditional_response_rate | 1 | 1 | 1 | 94 | 11 | synchronized_7d_process_time_block_all_pairs | 3 |  |  | equal change contributes to conditional FAR; unequal and opposite changes are positive asymmetry stress tests and never enter FAR | D4CAL-V16-e615cd349a49