## source_audit
temperature_source | temperature_sha256 | temperature_start | temperature_end | temperature_rows | temperature_raw_missing | temperature_invalid_range | temperature_valid_min_C | temperature_valid_max_C | study_minute_coverage | study_hour_with_30min_coverage | alignment | calibration_resolution | covariate_role | interpretation | saturation_equation | saturation_authority | saturation_reference_url | d1_filter_sheets | d1_optional_saturation_floor_filter | d1_sha256 | d2_sha256
整年对齐_分钟数据_2025-08-01_2026-07-30_01_influent+effluent.csv | 441d9dfd6d7273670ec11bd91588759f6784acfec78172b1ff2555d6fccc30af | 2025-08-01 | 2026-07-30 23:59 | 524160 | 4205 | 8 | 4.72 | 29.29 | 0.99018 | 0.99007 | exact_minute_no_interpolation_no_extrapolation | minute_calibration_minute_validation_minute_production | minute_influent_temperature_proxy | temperature_conditioned_operational_warning_not_thermodynamic_saturation_limit | Benson-Krause_1980_1984_equation_7 | USGS_DOTABLES_Technical_Memorandum_2011.03 | https://water.usgs.gov/water-resources/memos/documents/WQ.2011.03.pdf | not_used_by_primary_reference | not_applicable | not_consumed | not_consumed

## saturation_reference_check
temperature_C | Benson_Krause_Csat_mg_L | medium | pressure_atm | role
0 | 14.6208 | freshwater | 1 | temperature_normalizer_only
15 | 10.0839 | freshwater | 1 | temperature_normalizer_only
20 | 9.0924 | freshwater | 1 | temperature_normalizer_only
30 | 7.5588 | freshwater | 1 | temperature_normalizer_only
40 | 6.4127 | freshwater | 1 | temperature_normalizer_only

## frozen_registry_check
position | sensor_ids | n_calibration_sensor_minutes | registered_support_sensor_minutes | minimum_support_sensor_minutes | support_passed | ratio_median | ratio_mad_scale | ratio_p99 | recomputed_alpha | alpha_cluster_bootstrap_ci_low | alpha_cluster_bootstrap_ci_high | bootstrap_cluster | bootstrap_replicates | frozen_alpha | absolute_difference | registry_match | estimator | production_role
1 | DO_1_1,DO_2_1 | 521444 | 521444 | 43200 | TRUE | 0.07487 | 0.034721 | 0.34631 | 0.34631 | 0.28819 | 0.39639 | calendar_day | 1000 | 0.34631 | 2.1419e-11 | TRUE | max(P99,median+3x1.4826MAD)_of_minute_DO_over_Benson_Krause_Csat | frozen_operational_warning_only
2 | DO_1_2,DO_2_2 | 521461 | 521461 | 43200 | TRUE | 0.11171 | 0.042184 | 0.37156 | 0.37156 | 0.32635 | 0.42236 | calendar_day | 1000 | 0.37156 | 5.8055e-12 | TRUE | max(P99,median+3x1.4826MAD)_of_minute_DO_over_Benson_Krause_Csat | frozen_operational_warning_only
3 | DO_1_3,DO_2_3 | 521470 | 521470 | 43200 | TRUE | 0.25492 | 0.14218 | 0.54399 | 0.68145 | 0.61857 | 0.71843 | calendar_day | 1000 | 0.68145 | 1.4483e-11 | TRUE | max(P99,median+3x1.4826MAD)_of_minute_DO_over_Benson_Krause_Csat | frozen_operational_warning_only

## phase_validation
sensor_id | phase | n_evaluable_minutes | n_high_quality_minutes | dynamic_warning_count_all | dynamic_warning_count_high_quality | dynamic_warning_rate_all | dynamic_warning_rate_high_quality | dynamic_warning_rate_hq_ci_low | dynamic_warning_rate_hq_ci_high | n_2h_windows | n_2h_warning_windows | warning_2h_window_rate_high_quality | warning_2h_window_rate_ci_low | warning_2h_window_rate_ci_high | minute_criterion_pass | window_criterion_pass | joint_threshold_pass | promotion_assessment | median_dynamic_upper_mg_L | p05_dynamic_upper_mg_L | p95_dynamic_upper_mg_L | score_role
DO_1_1 | calibration | 260820 | 260716 | 1401 | 1401 | 0.0053715 | 0.0053737 | 0.0016515 | 0.0105 | 2174 | 39 | 0.017939 | 0.0087114 | 0.029092 | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_1_1 | terminal_test | 18318 | 18300 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_1_1 | validation | 84960 | 84960 | 2 | 2 | 2.354e-05 | 2.354e-05 | 0 | 5.8851e-05 | 708 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_1_2 | calibration | 260822 | 260735 | 1604 | 1604 | 0.0061498 | 0.0061518 | 0.0023145 | 0.010873 | 2174 | 46 | 0.021159 | 0.010119 | 0.036867 | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_1_2 | terminal_test | 18318 | 18300 | 11 | 11 | 0.0006005 | 0.00060109 | 0 | 0.0016783 | 153 | 1 | 0.0065359 | 0 | 0.019608 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_1_2 | validation | 84960 | 84960 | 11 | 11 | 0.00012947 | 0.00012947 | 0 | 0.00034193 | 708 | 1 | 0.0014124 | 0 | 0.0042373 | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_1_3 | calibration | 260819 | 260732 | 4 | 4 | 1.5336e-05 | 1.5341e-05 | 0 | 6.0767e-05 | 2174 | 1 | 0.00045998 | 0 | 0.0018307 | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_1_3 | terminal_test | 18318 | 18300 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_1_3 | validation | 84960 | 84960 | 0 | 0 | 0 | 0 | 0 | 0 | 708 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_2_1 | calibration | 260818 | 260728 | 3814 | 3814 | 0.014623 | 0.014628 | 0.006878 | 0.025449 | 2174 | 69 | 0.031739 | 0.020247 | 0.046716 | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_2_1 | terminal_test | 18318 | 18300 | 81 | 81 | 0.0044219 | 0.0044262 | 0 | 0.012676 | 153 | 4 | 0.026144 | 0 | 0.066667 | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_2_1 | validation | 84960 | 84960 | 50 | 50 | 0.00058851 | 0.00058851 | 0 | 0.0014595 | 708 | 3 | 0.0042373 | 0 | 0.009887 | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_2_2 | calibration | 260816 | 260726 | 3610 | 3610 | 0.013841 | 0.013846 | 0.0052929 | 0.023725 | 2174 | 55 | 0.025299 | 0.012908 | 0.037859 | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_2_2 | terminal_test | 18318 | 18300 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_2_2 | validation | 84960 | 84960 | 36 | 36 | 0.00042373 | 0.00042373 | 0 | 0.0012712 | 708 | 1 | 0.0014124 | 0 | 0.0042373 | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_2_3 | calibration | 260828 | 260738 | 300 | 300 | 0.0011502 | 0.0011506 | 0.0003521 | 0.0021298 | 2174 | 13 | 0.0059798 | 0.0031888 | 0.0095894 | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_2_3 | terminal_test | 18318 | 18300 | 19 | 19 | 0.0010372 | 0.0010383 | 0 | 0.0031879 | 153 | 1 | 0.0065359 | 0 | 0.02 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_2_3 | validation | 84960 | 84960 | 28 | 28 | 0.00032957 | 0.00032957 | 0 | 0.00071798 | 708 | 3 | 0.0042373 | 0 | 0.0084746 | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only

## reference_comparison
sensor_id | phase | n_evaluable_minutes | n_high_quality_minutes | dynamic_warning_count_all | dynamic_warning_count_high_quality | dynamic_warning_rate_all | dynamic_warning_rate_high_quality | dynamic_warning_rate_hq_ci_low | dynamic_warning_rate_hq_ci_high | n_2h_windows | n_2h_warning_windows | warning_2h_window_rate_high_quality | warning_2h_window_rate_ci_low | warning_2h_window_rate_ci_high | minute_criterion_pass | window_criterion_pass | joint_threshold_pass | promotion_assessment | median_dynamic_upper_mg_L | p05_dynamic_upper_mg_L | p95_dynamic_upper_mg_L | score_role | reference_route | evaluation_support
DO_1_1 | calibration | 260820 | 260716 | 1401 | 1401 | 0.0053715 | 0.0053737 | 0.0016515 | 0.0105 | 2174 | 39 | 0.017939 | 0.0087114 | 0.029092 | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_1_1 | terminal_test | 18318 | 18300 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_1_1 | validation | 84960 | 84960 | 2 | 2 | 2.354e-05 | 2.354e-05 | 0 | 5.8851e-05 | 708 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_1_2 | calibration | 260822 | 260735 | 1604 | 1604 | 0.0061498 | 0.0061518 | 0.0023145 | 0.010873 | 2174 | 46 | 0.021159 | 0.010119 | 0.036867 | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_1_2 | terminal_test | 18318 | 18300 | 11 | 11 | 0.0006005 | 0.00060109 | 0 | 0.0016783 | 153 | 1 | 0.0065359 | 0 | 0.019608 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_1_2 | validation | 84960 | 84960 | 11 | 11 | 0.00012947 | 0.00012947 | 0 | 0.00034193 | 708 | 1 | 0.0014124 | 0 | 0.0042373 | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_1_3 | calibration | 260819 | 260732 | 4 | 4 | 1.5336e-05 | 1.5341e-05 | 0 | 6.0767e-05 | 2174 | 1 | 0.00045998 | 0 | 0.0018307 | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only | neutral_primary | identical_neutral_minutes_and_windows
DO_1_3 | terminal_test | 18318 | 18300 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only | neutral_primary | identical_neutral_minutes_and_windows
DO_1_3 | validation | 84960 | 84960 | 0 | 0 | 0 | 0 | 0 | 0 | 708 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only | neutral_primary | identical_neutral_minutes_and_windows
DO_2_1 | calibration | 260818 | 260728 | 3814 | 3814 | 0.014623 | 0.014628 | 0.006878 | 0.025449 | 2174 | 69 | 0.031739 | 0.020247 | 0.046716 | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_2_1 | terminal_test | 18318 | 18300 | 81 | 81 | 0.0044219 | 0.0044262 | 0 | 0.012676 | 153 | 4 | 0.026144 | 0 | 0.066667 | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_2_1 | validation | 84960 | 84960 | 50 | 50 | 0.00058851 | 0.00058851 | 0 | 0.0014595 | 708 | 3 | 0.0042373 | 0 | 0.009887 | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_2_2 | calibration | 260816 | 260726 | 3610 | 3610 | 0.013841 | 0.013846 | 0.0052929 | 0.023725 | 2174 | 55 | 0.025299 | 0.012908 | 0.037859 | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_2_2 | terminal_test | 18318 | 18300 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_2_2 | validation | 84960 | 84960 | 36 | 36 | 0.00042373 | 0.00042373 | 0 | 0.0012712 | 708 | 1 | 0.0014124 | 0 | 0.0042373 | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning | neutral_primary | identical_neutral_minutes_and_windows
DO_2_3 | calibration | 260828 | 260738 | 300 | 300 | 0.0011502 | 0.0011506 | 0.0003521 | 0.0021298 | 2174 | 13 | 0.0059798 | 0.0031888 | 0.0095894 | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only | neutral_primary | identical_neutral_minutes_and_windows
DO_2_3 | terminal_test | 18318 | 18300 | 19 | 19 | 0.0010372 | 0.0010383 | 0 | 0.0031879 | 153 | 1 | 0.0065359 | 0 | 0.02 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only | neutral_primary | identical_neutral_minutes_and_windows
DO_2_3 | validation | 84960 | 84960 | 28 | 28 | 0.00032957 | 0.00032957 | 0 | 0.00071798 | 708 | 3 | 0.0042373 | 0 | 0.0084746 | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only | neutral_primary | identical_neutral_minutes_and_windows
DO_1_1 | calibration | 260820 | 260716 | 2955 | 2955 | 0.01133 | 0.011334 | 0.0041796 | 0.020906 | 2174 | 65 | 0.029899 | 0.017461 | 0.045749 | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 2.5621 | 2.1746 | 2.9221 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_1_1 | terminal_test | 18318 | 18300 | 12 | 12 | 0.00065509 | 0.00065574 | 0 | 0.00168 | 153 | 3 | 0.019608 | 0 | 0.052288 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 2.7151 | 2.673 | 2.7579 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_1_1 | validation | 84960 | 84960 | 84 | 84 | 0.0009887 | 0.0009887 | 0.00036488 | 0.0016831 | 708 | 7 | 0.009887 | 0.0042373 | 0.016949 | TRUE | TRUE | TRUE | pass | 2.8912 | 2.752 | 2.9702 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_1_2 | calibration | 260822 | 260735 | 4163 | 4163 | 0.015961 | 0.015966 | 0.0075091 | 0.025885 | 2174 | 96 | 0.044158 | 0.028055 | 0.064316 | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 2.8477 | 2.417 | 3.2478 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_1_2 | terminal_test | 18318 | 18300 | 341 | 341 | 0.018616 | 0.018634 | 0.0093975 | 0.02858 | 153 | 27 | 0.17647 | 0.098039 | 0.26144 | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.0178 | 2.971 | 3.0653 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_1_2 | validation | 84960 | 84960 | 223 | 223 | 0.0026248 | 0.0026248 | 0.0012585 | 0.0043909 | 708 | 19 | 0.026836 | 0.012712 | 0.043785 | TRUE | FALSE | FALSE | fail | 3.2134 | 3.0588 | 3.3013 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_1_3 | calibration | 260819 | 260732 | 282 | 282 | 0.0010812 | 0.0010816 | 1.5307e-05 | 0.0025811 | 2174 | 8 | 0.0036799 | 0.00046019 | 0.0078561 | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 4.6531 | 3.9493 | 5.3068 | diagnostic_only | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_1_3 | terminal_test | 18318 | 18300 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 4.931 | 4.8545 | 5.0086 | diagnostic_only | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_1_3 | validation | 84960 | 84960 | 11 | 11 | 0.00012947 | 0.00012947 | 0 | 0.00038842 | 708 | 1 | 0.0014124 | 0 | 0.0056497 | TRUE | TRUE | TRUE | pass | 5.2506 | 4.998 | 5.3942 | diagnostic_only | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_1 | calibration | 260818 | 260728 | 7069 | 7069 | 0.027103 | 0.027113 | 0.014386 | 0.042519 | 2174 | 126 | 0.057958 | 0.038211 | 0.080661 | FALSE | FALSE | FALSE | calibration_diagnostic_not_promotion | 2.5621 | 2.1746 | 2.9221 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_1 | terminal_test | 18318 | 18300 | 406 | 406 | 0.022164 | 0.022186 | 0.0043269 | 0.05196 | 153 | 10 | 0.065359 | 0.019231 | 0.11765 | FALSE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 2.7151 | 2.673 | 2.7579 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_1 | validation | 84960 | 84960 | 108 | 108 | 0.0012712 | 0.0012712 | 0.0003178 | 0.0025668 | 708 | 9 | 0.012712 | 0.0056497 | 0.022599 | TRUE | TRUE | TRUE | pass | 2.8912 | 2.752 | 2.9702 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_2 | calibration | 260816 | 260726 | 6214 | 6214 | 0.023825 | 0.023833 | 0.012412 | 0.03706 | 2174 | 105 | 0.048298 | 0.030644 | 0.066668 | FALSE | FALSE | FALSE | calibration_diagnostic_not_promotion | 2.8477 | 2.417 | 3.2478 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_2 | terminal_test | 18318 | 18300 | 13 | 13 | 0.00070968 | 0.00071038 | 0 | 0.0021311 | 153 | 1 | 0.0065359 | 0 | 0.019618 | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.0178 | 2.971 | 3.0653 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_2 | validation | 84960 | 84960 | 58 | 58 | 0.00068267 | 0.00068267 | 1.177e-05 | 0.0018244 | 708 | 3 | 0.0042373 | 0 | 0.009887 | TRUE | TRUE | TRUE | pass | 3.2134 | 3.0588 | 3.3013 | scored_operational_warning | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_3 | calibration | 260828 | 260738 | 13835 | 13835 | 0.053043 | 0.053061 | 0.040364 | 0.06795 | 2174 | 686 | 0.31555 | 0.27555 | 0.36836 | FALSE | FALSE | FALSE | calibration_diagnostic_not_promotion | 4.6531 | 3.9493 | 5.3068 | diagnostic_only | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_3 | terminal_test | 18318 | 18300 | 1868 | 1865 | 0.10198 | 0.10191 | 0.074093 | 0.13484 | 153 | 105 | 0.68627 | 0.54487 | 0.81699 | FALSE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 4.931 | 4.8545 | 5.0086 | diagnostic_only | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows
DO_2_3 | validation | 84960 | 84960 | 4420 | 4420 | 0.052024 | 0.052024 | 0.032579 | 0.074374 | 708 | 234 | 0.33051 | 0.24996 | 0.40685 | FALSE | FALSE | FALSE | fail | 5.2506 | 4.998 | 5.3942 | diagnostic_only | D1D2_screened_sensitivity | identical_neutral_minutes_and_windows

## cross_line_transfer
position | source_sensor | target_sensor | phase | source_calibration_minutes | source_only_alpha | target_high_quality_minutes | target_minute_warning_rate | n_2h_windows | n_2h_warning_windows | warning_2h_window_rate_high_quality | warning_2h_window_rate_ci_low | warning_2h_window_rate_ci_high | minute_criterion_pass | window_criterion_pass | role
1 | DO_1_1 | DO_2_1 | validation | 260716 | 0.30237 | 84960 | 0.00091808 | 708 | 5 | 0.0070621 | 0.0014124 | 0.014124 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning
1 | DO_1_1 | DO_2_1 | terminal_test | 260716 | 0.30237 | 18300 | 0.013497 | 153 | 6 | 0.039216 | 0 | 0.088481 | TRUE | FALSE | diagnostic_cross_line_transfer_not_used_for_tuning
1 | DO_2_1 | DO_1_1 | validation | 260728 | 0.37878 | 84960 | 0 | 708 | 0 | 0 | 0 | 0 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning
1 | DO_2_1 | DO_1_1 | terminal_test | 260728 | 0.37878 | 18300 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning
2 | DO_1_2 | DO_2_2 | validation | 260735 | 0.34207 | 84960 | 0.00044727 | 708 | 1 | 0.0014124 | 0 | 0.0042373 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning
2 | DO_1_2 | DO_2_2 | terminal_test | 260735 | 0.34207 | 18300 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning
2 | DO_2_2 | DO_1_2 | validation | 260726 | 0.40613 | 84960 | 8.2392e-05 | 708 | 1 | 0.0014124 | 0 | 0.0042373 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning
2 | DO_2_2 | DO_1_2 | terminal_test | 260726 | 0.40613 | 18300 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning
3 | DO_1_3 | DO_2_3 | validation | 260732 | 0.4286 | 84960 | 0.2719 | 708 | 504 | 0.71186 | 0.63415 | 0.78111 | FALSE | FALSE | diagnostic_cross_line_transfer_not_used_for_tuning
3 | DO_1_3 | DO_2_3 | terminal_test | 260732 | 0.4286 | 18300 | 0.47251 | 153 | 153 | 1 | 1 | 1 | FALSE | FALSE | diagnostic_cross_line_transfer_not_used_for_tuning
3 | DO_2_3 | DO_1_3 | validation | 260738 | 0.73423 | 84960 | 0 | 708 | 0 | 0 | 0 | 0 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning
3 | DO_2_3 | DO_1_3 | terminal_test | 260738 | 0.73423 | 18300 | 0 | 153 | 0 | 0 | 0 | 0 | TRUE | TRUE | diagnostic_cross_line_transfer_not_used_for_tuning

## alpha_sensitivity
sensor_id | phase | alpha_multiplier | n_evaluable_minutes | n_high_quality_minutes | dynamic_warning_count_all | dynamic_warning_count_high_quality | dynamic_warning_rate_all | dynamic_warning_rate_high_quality | dynamic_warning_rate_hq_ci_low | dynamic_warning_rate_hq_ci_high | n_2h_windows | n_2h_warning_windows | warning_2h_window_rate_high_quality | warning_2h_window_rate_ci_low | warning_2h_window_rate_ci_high | minute_criterion_pass | window_criterion_pass | joint_threshold_pass | promotion_assessment | median_dynamic_upper_mg_L | p05_dynamic_upper_mg_L | p95_dynamic_upper_mg_L | score_role
DO_1_1 | calibration | 0.8 | 260820 | 260716 | 2976 | 2976 | 0.01141 | 0.011415 |  |  | 2174 | 65 | 0.029899 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_1_1 | terminal_test | 0.8 | 18318 | 18300 | 14 | 14 | 0.00076428 | 0.00076503 |  |  | 153 | 3 | 0.019608 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_1_1 | validation | 0.8 | 84960 | 84960 | 87 | 87 | 0.001024 | 0.001024 |  |  | 708 | 7 | 0.009887 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_1_2 | calibration | 0.8 | 260822 | 260735 | 4942 | 4942 | 0.018948 | 0.018954 |  |  | 2174 | 126 | 0.057958 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_1_2 | terminal_test | 0.8 | 18318 | 18300 | 624 | 624 | 0.034065 | 0.034098 |  |  | 153 | 43 | 0.28105 |  |  | FALSE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_1_2 | validation | 0.8 | 84960 | 84960 | 460 | 460 | 0.0054143 | 0.0054143 |  |  | 708 | 37 | 0.05226 |  |  | TRUE | FALSE | FALSE | fail | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_1_3 | calibration | 0.8 | 260819 | 260732 | 203 | 203 | 0.00077832 | 0.00077858 |  |  | 2174 | 5 | 0.0022999 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_1_3 | terminal_test | 0.8 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_1_3 | validation | 0.8 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_2_1 | calibration | 0.8 | 260818 | 260728 | 7226 | 7226 | 0.027705 | 0.027715 |  |  | 2174 | 128 | 0.058878 |  |  | FALSE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_2_1 | terminal_test | 0.8 | 18318 | 18300 | 422 | 422 | 0.023037 | 0.02306 |  |  | 153 | 10 | 0.065359 |  |  | FALSE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_2_1 | validation | 0.8 | 84960 | 84960 | 113 | 113 | 0.00133 | 0.00133 |  |  | 708 | 10 | 0.014124 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_2_2 | calibration | 0.8 | 260816 | 260726 | 7019 | 7019 | 0.026912 | 0.026921 |  |  | 2174 | 121 | 0.055658 |  |  | FALSE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_2_2 | terminal_test | 0.8 | 18318 | 18300 | 25 | 25 | 0.0013648 | 0.0013661 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_2_2 | validation | 0.8 | 84960 | 84960 | 74 | 74 | 0.000871 | 0.000871 |  |  | 708 | 5 | 0.0070621 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_2_3 | calibration | 0.8 | 260828 | 260738 | 4836 | 4836 | 0.018541 | 0.018547 |  |  | 2174 | 325 | 0.14949 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_2_3 | terminal_test | 0.8 | 18318 | 18300 | 533 | 532 | 0.029097 | 0.029071 |  |  | 153 | 51 | 0.33333 |  |  | FALSE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_2_3 | validation | 0.8 | 84960 | 84960 | 1057 | 1057 | 0.012441 | 0.012441 |  |  | 708 | 97 | 0.13701 |  |  | TRUE | FALSE | FALSE | fail | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_1_1 | calibration | 0.9 | 260820 | 260716 | 2451 | 2451 | 0.0093973 | 0.009401 |  |  | 2174 | 52 | 0.023919 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_1_1 | terminal_test | 0.9 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_1_1 | validation | 0.9 | 84960 | 84960 | 19 | 19 | 0.00022363 | 0.00022363 |  |  | 708 | 2 | 0.0028249 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_1_2 | calibration | 0.9 | 260822 | 260735 | 2950 | 2950 | 0.01131 | 0.011314 |  |  | 2174 | 75 | 0.034499 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_1_2 | terminal_test | 0.9 | 18318 | 18300 | 104 | 104 | 0.0056775 | 0.0056831 |  |  | 153 | 10 | 0.065359 |  |  | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_1_2 | validation | 0.9 | 84960 | 84960 | 61 | 61 | 0.00071798 | 0.00071798 |  |  | 708 | 9 | 0.012712 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_1_3 | calibration | 0.9 | 260819 | 260732 | 23 | 23 | 8.8184e-05 | 8.8213e-05 |  |  | 2174 | 3 | 0.0013799 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_1_3 | terminal_test | 0.9 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_1_3 | validation | 0.9 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_2_1 | calibration | 0.9 | 260818 | 260728 | 4880 | 4880 | 0.01871 | 0.018717 |  |  | 2174 | 87 | 0.040018 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_2_1 | terminal_test | 0.9 | 18318 | 18300 | 225 | 225 | 0.012283 | 0.012295 |  |  | 153 | 5 | 0.03268 |  |  | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_2_1 | validation | 0.9 | 84960 | 84960 | 72 | 72 | 0.00084746 | 0.00084746 |  |  | 708 | 5 | 0.0070621 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_2_2 | calibration | 0.9 | 260816 | 260726 | 5036 | 5036 | 0.019309 | 0.019315 |  |  | 2174 | 70 | 0.032199 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_2_2 | terminal_test | 0.9 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_2_2 | validation | 0.9 | 84960 | 84960 | 41 | 41 | 0.00048258 | 0.00048258 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_2_3 | calibration | 0.9 | 260828 | 260738 | 600 | 600 | 0.0023004 | 0.0023012 |  |  | 2174 | 31 | 0.014259 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_2_3 | terminal_test | 0.9 | 18318 | 18300 | 28 | 28 | 0.0015286 | 0.0015301 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_2_3 | validation | 0.9 | 84960 | 84960 | 78 | 78 | 0.00091808 | 0.00091808 |  |  | 708 | 5 | 0.0070621 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_1_1 | calibration | 1 | 260820 | 260716 | 1401 | 1401 | 0.0053715 | 0.0053737 |  |  | 2174 | 39 | 0.017939 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_1_1 | terminal_test | 1 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_1_1 | validation | 1 | 84960 | 84960 | 2 | 2 | 2.354e-05 | 2.354e-05 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_1_2 | calibration | 1 | 260822 | 260735 | 1604 | 1604 | 0.0061498 | 0.0061518 |  |  | 2174 | 46 | 0.021159 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_1_2 | terminal_test | 1 | 18318 | 18300 | 11 | 11 | 0.0006005 | 0.00060109 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_1_2 | validation | 1 | 84960 | 84960 | 11 | 11 | 0.00012947 | 0.00012947 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_1_3 | calibration | 1 | 260819 | 260732 | 4 | 4 | 1.5336e-05 | 1.5341e-05 |  |  | 2174 | 1 | 0.00045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_1_3 | terminal_test | 1 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_1_3 | validation | 1 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_2_1 | calibration | 1 | 260818 | 260728 | 3814 | 3814 | 0.014623 | 0.014628 |  |  | 2174 | 69 | 0.031739 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_2_1 | terminal_test | 1 | 18318 | 18300 | 81 | 81 | 0.0044219 | 0.0044262 |  |  | 153 | 4 | 0.026144 |  |  | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_2_1 | validation | 1 | 84960 | 84960 | 50 | 50 | 0.00058851 | 0.00058851 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_2_2 | calibration | 1 | 260816 | 260726 | 3610 | 3610 | 0.013841 | 0.013846 |  |  | 2174 | 55 | 0.025299 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_2_2 | terminal_test | 1 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_2_2 | validation | 1 | 84960 | 84960 | 36 | 36 | 0.00042373 | 0.00042373 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_2_3 | calibration | 1 | 260828 | 260738 | 300 | 300 | 0.0011502 | 0.0011506 |  |  | 2174 | 13 | 0.0059798 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_2_3 | terminal_test | 1 | 18318 | 18300 | 19 | 19 | 0.0010372 | 0.0010383 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_2_3 | validation | 1 | 84960 | 84960 | 28 | 28 | 0.00032957 | 0.00032957 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_1_1 | calibration | 1.1 | 260820 | 260716 | 1120 | 1120 | 0.0042941 | 0.0042959 |  |  | 2174 | 30 | 0.013799 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_1_1 | terminal_test | 1.1 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_1_1 | validation | 1.1 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_1_2 | calibration | 1.1 | 260822 | 260735 | 1042 | 1042 | 0.0039951 | 0.0039964 |  |  | 2174 | 31 | 0.014259 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_1_2 | terminal_test | 1.1 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_1_2 | validation | 1.1 | 84960 | 84960 | 7 | 7 | 8.2392e-05 | 8.2392e-05 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_1_3 | calibration | 1.1 | 260819 | 260732 | 4 | 4 | 1.5336e-05 | 1.5341e-05 |  |  | 2174 | 1 | 0.00045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_1_3 | terminal_test | 1.1 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_1_3 | validation | 1.1 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_2_1 | calibration | 1.1 | 260818 | 260728 | 2535 | 2535 | 0.0097194 | 0.0097228 |  |  | 2174 | 54 | 0.024839 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_2_1 | terminal_test | 1.1 | 18318 | 18300 | 23 | 23 | 0.0012556 | 0.0012568 |  |  | 153 | 2 | 0.013072 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_2_1 | validation | 1.1 | 84960 | 84960 | 46 | 46 | 0.00054143 | 0.00054143 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_2_2 | calibration | 1.1 | 260816 | 260726 | 2536 | 2536 | 0.0097233 | 0.0097267 |  |  | 2174 | 38 | 0.017479 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_2_2 | terminal_test | 1.1 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_2_2 | validation | 1.1 | 84960 | 84960 | 32 | 32 | 0.00037665 | 0.00037665 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_2_3 | calibration | 1.1 | 260828 | 260738 | 132 | 132 | 0.00050608 | 0.00050626 |  |  | 2174 | 10 | 0.0045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_2_3 | terminal_test | 1.1 | 18318 | 18300 | 18 | 18 | 0.00098264 | 0.00098361 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_2_3 | validation | 1.1 | 84960 | 84960 | 24 | 24 | 0.00028249 | 0.00028249 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_1_1 | calibration | 1.2 | 260820 | 260716 | 943 | 943 | 0.0036155 | 0.003617 |  |  | 2174 | 26 | 0.01196 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_1_1 | terminal_test | 1.2 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_1_1 | validation | 1.2 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_1_2 | calibration | 1.2 | 260822 | 260735 | 831 | 831 | 0.0031861 | 0.0031871 |  |  | 2174 | 17 | 0.0078197 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_1_2 | terminal_test | 1.2 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_1_2 | validation | 1.2 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_1_3 | calibration | 1.2 | 260819 | 260732 | 3 | 3 | 1.1502e-05 | 1.1506e-05 |  |  | 2174 | 1 | 0.00045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_1_3 | terminal_test | 1.2 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_1_3 | validation | 1.2 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only
DO_2_1 | calibration | 1.2 | 260818 | 260728 | 1752 | 1752 | 0.0067173 | 0.0067196 |  |  | 2174 | 37 | 0.017019 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning
DO_2_1 | terminal_test | 1.2 | 18318 | 18300 | 20 | 20 | 0.0010918 | 0.0010929 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning
DO_2_1 | validation | 1.2 | 84960 | 84960 | 42 | 42 | 0.00049435 | 0.00049435 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning
DO_2_2 | calibration | 1.2 | 260816 | 260726 | 1709 | 1709 | 0.0065525 | 0.0065548 |  |  | 2174 | 28 | 0.012879 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning
DO_2_2 | terminal_test | 1.2 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning
DO_2_2 | validation | 1.2 | 84960 | 84960 | 29 | 29 | 0.00034134 | 0.00034134 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning
DO_2_3 | calibration | 1.2 | 260828 | 260738 | 125 | 125 | 0.00047924 | 0.00047941 |  |  | 2174 | 10 | 0.0045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only
DO_2_3 | terminal_test | 1.2 | 18318 | 18300 | 16 | 16 | 0.00087346 | 0.00087432 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only
DO_2_3 | validation | 1.2 | 84960 | 84960 | 21 | 21 | 0.00024718 | 0.00024718 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only

## alpha_CI_scenarios
sensor_id | phase | alpha_scenario | alpha_value | n_evaluable_minutes | n_high_quality_minutes | dynamic_warning_count_all | dynamic_warning_count_high_quality | dynamic_warning_rate_all | dynamic_warning_rate_high_quality | dynamic_warning_rate_hq_ci_low | dynamic_warning_rate_hq_ci_high | n_2h_windows | n_2h_warning_windows | warning_2h_window_rate_high_quality | warning_2h_window_rate_ci_low | warning_2h_window_rate_ci_high | minute_criterion_pass | window_criterion_pass | joint_threshold_pass | promotion_assessment | median_dynamic_upper_mg_L | p05_dynamic_upper_mg_L | p95_dynamic_upper_mg_L | score_role | sensitivity_role
DO_1_1 | calibration | bootstrap_lower | 0.28819 | 260820 | 260716 | 2820 | 2820 | 0.010812 | 0.010816 |  |  | 2174 | 63 | 0.028979 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 2.6472 | 2.2468 | 3.0191 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_1 | terminal_test | bootstrap_lower | 0.28819 | 18318 | 18300 | 3 | 3 | 0.00016377 | 0.00016393 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 2.8053 | 2.7617 | 2.8494 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_1 | validation | bootstrap_lower | 0.28819 | 84960 | 84960 | 56 | 56 | 0.00065913 | 0.00065913 |  |  | 708 | 6 | 0.0084746 |  |  | TRUE | TRUE | TRUE | pass | 2.9871 | 2.8434 | 3.0688 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | calibration | bootstrap_lower | 0.32635 | 260822 | 260735 | 3310 | 3310 | 0.012691 | 0.012695 |  |  | 2174 | 79 | 0.036339 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 2.9977 | 2.5443 | 3.4188 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | terminal_test | bootstrap_lower | 0.32635 | 18318 | 18300 | 151 | 151 | 0.0082433 | 0.0082514 |  |  | 153 | 13 | 0.084967 |  |  | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.1767 | 3.1274 | 3.2267 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | validation | bootstrap_lower | 0.32635 | 84960 | 84960 | 89 | 89 | 0.0010476 | 0.0010476 |  |  | 708 | 11 | 0.015537 |  |  | TRUE | TRUE | TRUE | pass | 3.3826 | 3.2199 | 3.4751 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | calibration | bootstrap_lower | 0.61857 | 260819 | 260732 | 20 | 20 | 7.6682e-05 | 7.6707e-05 |  |  | 2174 | 2 | 0.00091996 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 5.6818 | 4.8224 | 6.48 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | terminal_test | bootstrap_lower | 0.61857 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.0211 | 5.9277 | 6.1159 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | validation | bootstrap_lower | 0.61857 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 6.4114 | 6.1029 | 6.5868 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | calibration | bootstrap_lower | 0.28819 | 260818 | 260728 | 6281 | 6281 | 0.024082 | 0.02409 |  |  | 2174 | 112 | 0.051518 |  |  | FALSE | FALSE | FALSE | calibration_diagnostic_not_promotion | 2.6472 | 2.2468 | 3.0191 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | terminal_test | bootstrap_lower | 0.28819 | 18318 | 18300 | 322 | 322 | 0.017578 | 0.017596 |  |  | 153 | 10 | 0.065359 |  |  | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 2.8053 | 2.7617 | 2.8494 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | validation | bootstrap_lower | 0.28819 | 84960 | 84960 | 95 | 95 | 0.0011182 | 0.0011182 |  |  | 708 | 7 | 0.009887 |  |  | TRUE | TRUE | TRUE | pass | 2.9871 | 2.8434 | 3.0688 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | calibration | bootstrap_lower | 0.32635 | 260816 | 260726 | 5370 | 5370 | 0.020589 | 0.020596 |  |  | 2174 | 79 | 0.036339 |  |  | FALSE | FALSE | FALSE | calibration_diagnostic_not_promotion | 2.9977 | 2.5443 | 3.4188 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | terminal_test | bootstrap_lower | 0.32635 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.1767 | 3.1274 | 3.2267 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | validation | bootstrap_lower | 0.32635 | 84960 | 84960 | 47 | 47 | 0.0005532 | 0.0005532 |  |  | 708 | 2 | 0.0028249 |  |  | TRUE | TRUE | TRUE | pass | 3.3826 | 3.2199 | 3.4751 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | calibration | bootstrap_lower | 0.61857 | 260828 | 260738 | 554 | 554 | 0.002124 | 0.0021247 |  |  | 2174 | 28 | 0.012879 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 5.6818 | 4.8224 | 6.48 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | terminal_test | bootstrap_lower | 0.61857 | 18318 | 18300 | 24 | 24 | 0.0013102 | 0.0013115 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.0211 | 5.9277 | 6.1159 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | validation | bootstrap_lower | 0.61857 | 84960 | 84960 | 69 | 69 | 0.00081215 | 0.00081215 |  |  | 708 | 5 | 0.0070621 |  |  | TRUE | TRUE | TRUE | pass | 6.4114 | 6.1029 | 6.5868 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_1 | calibration | point_estimate | 0.34631 | 260820 | 260716 | 1401 | 1401 | 0.0053715 | 0.0053737 |  |  | 2174 | 39 | 0.017939 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_1 | terminal_test | point_estimate | 0.34631 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_1 | validation | point_estimate | 0.34631 | 84960 | 84960 | 2 | 2 | 2.354e-05 | 2.354e-05 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | calibration | point_estimate | 0.37156 | 260822 | 260735 | 1604 | 1604 | 0.0061498 | 0.0061518 |  |  | 2174 | 46 | 0.021159 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | terminal_test | point_estimate | 0.37156 | 18318 | 18300 | 11 | 11 | 0.0006005 | 0.00060109 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | validation | point_estimate | 0.37156 | 84960 | 84960 | 11 | 11 | 0.00012947 | 0.00012947 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | calibration | point_estimate | 0.68145 | 260819 | 260732 | 4 | 4 | 1.5336e-05 | 1.5341e-05 |  |  | 2174 | 1 | 0.00045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | terminal_test | point_estimate | 0.68145 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | validation | point_estimate | 0.68145 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | calibration | point_estimate | 0.34631 | 260818 | 260728 | 3814 | 3814 | 0.014623 | 0.014628 |  |  | 2174 | 69 | 0.031739 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | terminal_test | point_estimate | 0.34631 | 18318 | 18300 | 81 | 81 | 0.0044219 | 0.0044262 |  |  | 153 | 4 | 0.026144 |  |  | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | validation | point_estimate | 0.34631 | 84960 | 84960 | 50 | 50 | 0.00058851 | 0.00058851 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | calibration | point_estimate | 0.37156 | 260816 | 260726 | 3610 | 3610 | 0.013841 | 0.013846 |  |  | 2174 | 55 | 0.025299 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | terminal_test | point_estimate | 0.37156 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | validation | point_estimate | 0.37156 | 84960 | 84960 | 36 | 36 | 0.00042373 | 0.00042373 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | calibration | point_estimate | 0.68145 | 260828 | 260738 | 300 | 300 | 0.0011502 | 0.0011506 |  |  | 2174 | 13 | 0.0059798 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | terminal_test | point_estimate | 0.68145 | 18318 | 18300 | 19 | 19 | 0.0010372 | 0.0010383 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | validation | point_estimate | 0.68145 | 84960 | 84960 | 28 | 28 | 0.00032957 | 0.00032957 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_1 | calibration | bootstrap_upper | 0.39639 | 260820 | 260716 | 1043 | 1043 | 0.0039989 | 0.0040005 |  |  | 2174 | 27 | 0.01242 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.641 | 3.0903 | 4.1525 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_1 | terminal_test | bootstrap_upper | 0.39639 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.8584 | 3.7986 | 3.9192 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_1 | validation | bootstrap_upper | 0.39639 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 4.1086 | 3.9109 | 4.221 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | calibration | bootstrap_upper | 0.42236 | 260822 | 260735 | 935 | 935 | 0.0035848 | 0.003586 |  |  | 2174 | 21 | 0.0096596 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.8795 | 3.2927 | 4.4245 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | terminal_test | bootstrap_upper | 0.42236 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 4.1112 | 4.0474 | 4.1759 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_2 | validation | bootstrap_upper | 0.42236 | 84960 | 84960 | 3 | 3 | 3.5311e-05 | 3.5311e-05 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 4.3777 | 4.1671 | 4.4974 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | calibration | bootstrap_upper | 0.71843 | 260819 | 260732 | 4 | 4 | 1.5336e-05 | 1.5341e-05 |  |  | 2174 | 1 | 0.00045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.599 | 5.6009 | 7.5261 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | terminal_test | bootstrap_upper | 0.71843 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.9931 | 6.8846 | 7.1032 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_1_3 | validation | bootstrap_upper | 0.71843 | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 7.4465 | 7.0881 | 7.6501 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | calibration | bootstrap_upper | 0.39639 | 260818 | 260728 | 2149 | 2149 | 0.0082395 | 0.0082423 |  |  | 2174 | 44 | 0.020239 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.641 | 3.0903 | 4.1525 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | terminal_test | bootstrap_upper | 0.39639 | 18318 | 18300 | 20 | 20 | 0.0010918 | 0.0010929 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.8584 | 3.7986 | 3.9192 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_1 | validation | bootstrap_upper | 0.39639 | 84960 | 84960 | 45 | 45 | 0.00052966 | 0.00052966 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 4.1086 | 3.9109 | 4.221 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | calibration | bootstrap_upper | 0.42236 | 260816 | 260726 | 2228 | 2228 | 0.0085424 | 0.0085454 |  |  | 2174 | 33 | 0.015179 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.8795 | 3.2927 | 4.4245 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | terminal_test | bootstrap_upper | 0.42236 | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 4.1112 | 4.0474 | 4.1759 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_2 | validation | bootstrap_upper | 0.42236 | 84960 | 84960 | 31 | 31 | 0.00036488 | 0.00036488 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 4.3777 | 4.1671 | 4.4974 | scored_operational_warning | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | calibration | bootstrap_upper | 0.71843 | 260828 | 260738 | 170 | 170 | 0.00065177 | 0.000652 |  |  | 2174 | 13 | 0.0059798 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.599 | 5.6009 | 7.5261 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | terminal_test | bootstrap_upper | 0.71843 | 18318 | 18300 | 19 | 19 | 0.0010372 | 0.0010383 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.9931 | 6.8846 | 7.1032 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection
DO_2_3 | validation | bootstrap_upper | 0.71843 | 84960 | 84960 | 24 | 24 | 0.00028249 | 0.00028249 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 7.4465 | 7.0881 | 7.6501 | diagnostic_only | bootstrap_interval_propagation_not_production_parameter_selection

## envelope_comparison
sensor_id | phase | envelope_model | n_evaluable_minutes | n_high_quality_minutes | dynamic_warning_count_all | dynamic_warning_count_high_quality | dynamic_warning_rate_all | dynamic_warning_rate_high_quality | dynamic_warning_rate_hq_ci_low | dynamic_warning_rate_hq_ci_high | n_2h_windows | n_2h_warning_windows | warning_2h_window_rate_high_quality | warning_2h_window_rate_ci_low | warning_2h_window_rate_ci_high | minute_criterion_pass | window_criterion_pass | joint_threshold_pass | promotion_assessment | median_dynamic_upper_mg_L | p05_dynamic_upper_mg_L | p95_dynamic_upper_mg_L | score_role | comparison_role
DO_1_1 | calibration | temperature_conditioned | 260820 | 260716 | 1401 | 1401 | 0.0053715 | 0.0053737 |  |  | 2174 | 39 | 0.017939 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_1 | terminal_test | temperature_conditioned | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_1 | validation | temperature_conditioned | 84960 | 84960 | 2 | 2 | 2.354e-05 | 2.354e-05 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_2 | calibration | temperature_conditioned | 260822 | 260735 | 1604 | 1604 | 0.0061498 | 0.0061518 |  |  | 2174 | 46 | 0.021159 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_2 | terminal_test | temperature_conditioned | 18318 | 18300 | 11 | 11 | 0.0006005 | 0.00060109 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_2 | validation | temperature_conditioned | 84960 | 84960 | 11 | 11 | 0.00012947 | 0.00012947 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_3 | calibration | temperature_conditioned | 260819 | 260732 | 4 | 4 | 1.5336e-05 | 1.5341e-05 |  |  | 2174 | 1 | 0.00045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_1_3 | terminal_test | temperature_conditioned | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_1_3 | validation | temperature_conditioned | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_2_1 | calibration | temperature_conditioned | 260818 | 260728 | 3814 | 3814 | 0.014623 | 0.014628 |  |  | 2174 | 69 | 0.031739 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.181 | 2.6999 | 3.6279 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_1 | terminal_test | temperature_conditioned | 18318 | 18300 | 81 | 81 | 0.0044219 | 0.0044262 |  |  | 153 | 4 | 0.026144 |  |  | TRUE | FALSE | FALSE | locked_forward_test_not_used_for_selection | 3.371 | 3.3187 | 3.4241 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_1 | validation | temperature_conditioned | 84960 | 84960 | 50 | 50 | 0.00058851 | 0.00058851 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 3.5895 | 3.4168 | 3.6877 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_2 | calibration | temperature_conditioned | 260816 | 260726 | 3610 | 3610 | 0.013841 | 0.013846 |  |  | 2174 | 55 | 0.025299 |  |  | TRUE | FALSE | FALSE | calibration_diagnostic_not_promotion | 3.4129 | 2.8967 | 3.8924 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_2 | terminal_test | temperature_conditioned | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 3.6167 | 3.5606 | 3.6737 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_2 | validation | temperature_conditioned | 84960 | 84960 | 36 | 36 | 0.00042373 | 0.00042373 |  |  | 708 | 1 | 0.0014124 |  |  | TRUE | TRUE | TRUE | pass | 3.8512 | 3.6659 | 3.9566 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_3 | calibration | temperature_conditioned | 260828 | 260738 | 300 | 300 | 0.0011502 | 0.0011506 |  |  | 2174 | 13 | 0.0059798 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 6.2594 | 5.3126 | 7.1387 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_2_3 | terminal_test | temperature_conditioned | 18318 | 18300 | 19 | 19 | 0.0010372 | 0.0010383 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 6.6332 | 6.5302 | 6.7376 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_2_3 | validation | temperature_conditioned | 84960 | 84960 | 28 | 28 | 0.00032957 | 0.00032957 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 7.0632 | 6.7233 | 7.2564 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_1_1 | calibration | fixed_8_mg_L | 260820 | 260716 | 93 | 93 | 0.00035657 | 0.00035671 |  |  | 2174 | 6 | 0.0027599 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_1 | terminal_test | fixed_8_mg_L | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_1 | validation | fixed_8_mg_L | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_2 | calibration | fixed_8_mg_L | 260822 | 260735 | 86 | 86 | 0.00032973 | 0.00032984 |  |  | 2174 | 5 | 0.0022999 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_2 | terminal_test | fixed_8_mg_L | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_2 | validation | fixed_8_mg_L | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_1_3 | calibration | fixed_8_mg_L | 260819 | 260732 | 3 | 3 | 1.1502e-05 | 1.1506e-05 |  |  | 2174 | 1 | 0.00045998 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 8 | 8 | 8 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_1_3 | terminal_test | fixed_8_mg_L | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 8 | 8 | 8 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_1_3 | validation | fixed_8_mg_L | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 8 | 8 | 8 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_2_1 | calibration | fixed_8_mg_L | 260818 | 260728 | 62 | 62 | 0.00023771 | 0.0002378 |  |  | 2174 | 7 | 0.0032199 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_1 | terminal_test | fixed_8_mg_L | 18318 | 18300 | 15 | 15 | 0.00081887 | 0.00081967 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_1 | validation | fixed_8_mg_L | 84960 | 84960 | 19 | 19 | 0.00022363 | 0.00022363 |  |  | 708 | 2 | 0.0028249 |  |  | TRUE | TRUE | TRUE | pass | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_2 | calibration | fixed_8_mg_L | 260816 | 260726 | 0 | 0 | 0 | 0 |  |  | 2174 | 0 | 0 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_2 | terminal_test | fixed_8_mg_L | 18318 | 18300 | 0 | 0 | 0 | 0 |  |  | 153 | 0 | 0 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_2 | validation | fixed_8_mg_L | 84960 | 84960 | 0 | 0 | 0 | 0 |  |  | 708 | 0 | 0 |  |  | TRUE | TRUE | TRUE | pass | 8 | 8 | 8 | scored_operational_warning | prespecified_method_comparison_not_threshold_selection
DO_2_3 | calibration | fixed_8_mg_L | 260828 | 260738 | 117 | 117 | 0.00044857 | 0.00044873 |  |  | 2174 | 9 | 0.0041398 |  |  | TRUE | TRUE | TRUE | calibration_diagnostic_not_promotion | 8 | 8 | 8 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_2_3 | terminal_test | fixed_8_mg_L | 18318 | 18300 | 16 | 16 | 0.00087346 | 0.00087432 |  |  | 153 | 1 | 0.0065359 |  |  | TRUE | TRUE | TRUE | locked_forward_test_not_used_for_selection | 8 | 8 | 8 | diagnostic_only | prespecified_method_comparison_not_threshold_selection
DO_2_3 | validation | fixed_8_mg_L | 84960 | 84960 | 24 | 24 | 0.00028249 | 0.00028249 |  |  | 708 | 3 | 0.0042373 |  |  | TRUE | TRUE | TRUE | pass | 8 | 8 | 8 | diagnostic_only | prespecified_method_comparison_not_threshold_selection

## exclusions
phase | sensor_id | exclusion | n_sensor_minutes
calibration | DO_1_1 | DO_unavailable | 520
calibration | DO_1_1 | eligible | 260716
calibration | DO_1_1 | neutral_reference_criteria_failed | 104
calibration | DO_1_1 | temperature_unavailable | 3620
calibration | DO_1_2 | DO_unavailable | 518
calibration | DO_1_2 | eligible | 260735
calibration | DO_1_2 | neutral_reference_criteria_failed | 87
calibration | DO_1_2 | temperature_unavailable | 3620
calibration | DO_1_3 | DO_unavailable | 521
calibration | DO_1_3 | eligible | 260732
calibration | DO_1_3 | neutral_reference_criteria_failed | 87
calibration | DO_1_3 | temperature_unavailable | 3620
calibration | DO_2_1 | DO_unavailable | 522
calibration | DO_2_1 | eligible | 260728
calibration | DO_2_1 | neutral_reference_criteria_failed | 90
calibration | DO_2_1 | temperature_unavailable | 3620
calibration | DO_2_2 | DO_unavailable | 524
calibration | DO_2_2 | eligible | 260726
calibration | DO_2_2 | neutral_reference_criteria_failed | 90
calibration | DO_2_2 | temperature_unavailable | 3620
calibration | DO_2_3 | DO_unavailable | 512
calibration | DO_2_3 | eligible | 260738
calibration | DO_2_3 | neutral_reference_criteria_failed | 90
calibration | DO_2_3 | temperature_unavailable | 3620
terminal_test | DO_1_1 | DO_unavailable | 402
terminal_test | DO_1_1 | eligible | 18300
terminal_test | DO_1_1 | neutral_reference_criteria_failed | 18
terminal_test | DO_1_2 | DO_unavailable | 402
terminal_test | DO_1_2 | eligible | 18300
terminal_test | DO_1_2 | neutral_reference_criteria_failed | 18
terminal_test | DO_1_3 | DO_unavailable | 402
terminal_test | DO_1_3 | eligible | 18300
terminal_test | DO_1_3 | neutral_reference_criteria_failed | 18
terminal_test | DO_2_1 | DO_unavailable | 402
terminal_test | DO_2_1 | eligible | 18300
terminal_test | DO_2_1 | neutral_reference_criteria_failed | 18
terminal_test | DO_2_2 | DO_unavailable | 402
terminal_test | DO_2_2 | eligible | 18300
terminal_test | DO_2_2 | neutral_reference_criteria_failed | 18
terminal_test | DO_2_3 | DO_unavailable | 402
terminal_test | DO_2_3 | eligible | 18300
terminal_test | DO_2_3 | neutral_reference_criteria_failed | 18
validation | DO_1_1 | eligible | 84960
validation | DO_1_2 | eligible | 84960
validation | DO_1_3 | eligible | 84960
validation | DO_2_1 | eligible | 84960
validation | DO_2_2 | eligible | 84960
validation | DO_2_3 | eligible | 84960